## INTRODUCTION
Modbus description is valid for Modbus RTU and Modbus TCP communication
Modbus communication description is valid for all product types
Before controlling the product over the Modbus, it is necessary to read manual for the product to know exact supported functionalities of product in all modes!!!
Usage of specific registers depend on hardware product configuration (water heated, electrically heated, rotary wheel exchanger, plate exchanger, bypass used or not,...) and as well also on actual used mode and settings in service menu (Room sensor or Inlet sensor,....)
Each list in the document contain the same type of registers wich are used for the same purpose (example bellow)
Example 1: SHARE = holding registers (READ/WRITE - orange colour of the list) - used for control the product
Example 2: STATUS AHU = input registers (READ only registers - blue colour of the list) - used to read out actual status of the product
In each list of registers, there is an additional colour marking of each register showing the usage of register for the specific product type (uncoloured = usage for all product, Green colour = registers only for AHU and HRU units, Orange = registers for Air curtains, IC controllers and SC controllers)
Description of registers purpose in each list :
HOLDING REGISTERS - READ/WRITE | Purpose:
FACTORY_DRIVER | Used for manufacturer purpose
FACTORY_SET | Used for manufacturer purpose
SERVICE | To set and check parameters in service menu of the product. Factory reset function, resets the parameters to default values
SERVICE_HARD | To set and check parameters in service menu of the product. Factory reset function, keep the preset parameters (connected hardware configuration is kept). To reset the parameters to default it is necessary to proceed FACTORY HARD reset.
SHARE | Used for product control. Registers represent actual control commands and allows sending the control requests to the product. Registers also represent the commands from control panel or other control equipment (Android app, Service SW,...)
TIME_DRIVER | To set actual time in controller
TIME_SWITCH_WEEK | To set and check actual settings for week time schedule
TIME_SWITCH_YEAR | To set and check actual settings for year time schedule
ERROR_LOG_AHU | To read error log memory for AHU and HRU units (WRITE function will not be proceeded)
ERROR_LOG_AC | To read error log memory for AIR curtians, IC and SC controllers (WRITE function will not be proceeded)
ERROR_LOG_DRIVER | Registers for management of error log reading (BUFFER selection, BANK selection, Clearing error log memory command)
NETWORK | To setup and check NETWORK
CFG_UNIT | To read out the product configuration. (WRITE function will be not proceeded)
WIFI_SETTINGS | Used for manufacturer purpose
DIRECT_CONTROL | To test HW of the controller. To be able use this registers, it is necessary to activate "Direct control mode" in SHARE
NORDIC_SERVICE | To setup additional service menu functions for Air curtains, IC and SC controller
MODE_ERROR_RELAY | To setup selection of errors whose will be used for error signalisation by relay output ERROR
INPUT REGISTERS - READ ONLY
INFO | To read out informations about the product (same as info screen from control panel)
STATUS_AHU | To read out actul status of the AHU and HRU units (actual mode, air flows, temperatures, HW status, Errors,…)
STATUS_AC | To read out actul status of the air curtain, IC controller or SC controller (actual mode, air flows, temperatures, HW status, Errors,…)
SLAVE_AC_STATUS | To read out actul status of the SLAVE air curtains, SLAVE IC controllers or SLAVE SC controllers (actual mode, fan speed, temperatures, HW status, Errors,…)
TIME | To check actual time in controller

## FUNCTIONS
HOLDING REGISTERS | FUNC_CODE
FACTORY_DRIVER | 0x03,0x06,0x10
FACTORY_SET | 0x03,0x06,0x10
SERVICE | 0x03,0x06,0x10
SERVICE_HARD | 0x03,0x06,0x10
SHARE | 0x03,0x06,0x10
TIME_DRIVER | 0x03,0x06,0x10
TIME_SWITCH_WEEK | 0x03,0x06,0x10
TIME_SWITCH_YEAR | 0x03,0x06,0x10
ERROR_LOG_AHU | 0x03,0x06,0x10
ERROR_LOG_AC | 0x03,0x06,0x10
ERROR_LOG_DRIVER | 0x03,0x06,0x10
NETWORK | 0x03,0x06,0x10
CFG_UNIT | 0x03,0x06,0x10
WIFI_SETTINGS | 0x03,0x06,0x10
DIRECT_CONTROL | 0x03,0x06,0x10
NORDIC_SERVICE | 0x03,0x06,0x10
MODE_ERROR_RELAY | 0x03,0x06,0x10
INPUT REGISTERS
INFO | 0x04
STATUS_AHU | 0x04
STATUS_AC | 0x04
SLAVE_AC_STATUS | 0x04
TIME | 0x04
Default Modbus RTU settings
Modbus Unit Address | 1
Baudrate | 9600
Parity | ODD
Stop Bits | 1
PLC Addresses - BASE1
Default Modbus TCP port
Default port | 502
NOTE:
Used for HRU and AHU -green
Used for Air curtains, IC controllers and SC controllers - orange
Used for all products - without color marking
Values are represent as unsigned 2xByte

## FACTORY_DRIVER (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Factory_driver register - without valid FactoryPass only read (Factory reset no effect)
10000 | FactoryPass |  |  | 0 | 0xFFFF | 0
10001 | FactoryReset |  | 0 - non 1 - active | 0 | 1 | 0 | RESET_NON ACTIVE
10002 | HardFactoryReset |  | 0 - non 1 - active | 0 | 1 | 0 | RESET_NON ACTIVE
10003 | SWReset |  | 0 - non 1 - active | 0 | 1 | 0 | RESET_NON ACTIVE
10004 | FwMbUpdateFlag |  | 0 - non 0xAB16- request | 0 | 0xFFFF | 0 | UPDATEFLAG_NON REQUEST
10005 | FwCpUpdateFlag |  | 0 - non 0xAB17 - request | 0 | 0xFFFF | 0 | UPDATEFLAG_NON REQUEST

## FACTORY_SET
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Factory_set register - without valid FactoryPass only read (Factory reset no effect)
10100 | FactoryPass |  |  | 0 | 0xFFFF | 0
10101 | Mode |  | 0-2vv 1-FranceAir 2-USA 3-Helios | 0 | 3 | 0 | HOME_2VV USA FRANCEAIR HELIOS
10102 | Locality |  | 0-EU 1-USA | 0 | 1 | 0 | LOC_EU LOC_USA
10103 | ModuleB |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10104 | Module1W |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10105 | ModuleEnergyMeasure |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10106 | ModuleRotaryRecup |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10107 | ModuleAC3 |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10108 | ModuleAC5 |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10109 | ModuleAC5_400 |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10110 | EhternetModule |  | 0 - non 1 - fitted | 0 | 1 | 1 | MODULE_NON FITTED
10111 | MaxFlowManual |  | ‰ of fan power | 700 | 1000 | 1000
10112 | MinFlowManual |  | ‰ of fan power | 0 | 400 | 200
10113 | StepFlowManual |  | ‰ of fan power | 10 | 200 | 100
10114 | MaxFlow |  | m3/h (cfm) | 150 (90) | 700 (420) | 150 (100) | 150 (90) 300 (180) 500 (300) 700 (420)
10115 | MinFlow |  | m3/h (cfm) | 40 (20) | 140 (80) | 40 (20) | 40 (20) 70 (40) 100 (60) 140 (80)
10116 | StepFlow |  | m3/h (cfm) | 11 (6) | 56 (32) | 11 (6) | 11 (6) 23 (13) 40 (23) 56 (32)
10117 | UnitSpecif |  | 0 - vertical 1 - horizontal 2- flat 3 - rooftop 4 - wall | 0 | 4 | 4 | VERTICAL HORIZONTAL FLAT ROOFTOP WALL
10118 | Preheater_set_1 |  | 0 - PWM 1 - analog | 0 | 1 | 1 | SET_PWM SET_ANALOG
10119 | Preheater_1 |  | 0 - none 1 - electric 2 - water | 0 | 2 | 0 | PRE_NON PRE_ELECTRIC PRE_WATER
10120 | Preheater_set_2 |  | 0 - PWM 1 - analog | 0 | 1 | 1 | SET_PWM SET_ANALOG
10121 | Preheater_2 |  | 0 - none 1 - electric 2 - water | 0 | 2 | 0 | PRE_NON PRE_ELECTRIC PRE_WATER
10122 | Postheat_set_1 |  | 0 - PWM 1 - analog | 0 | 1 | 0 | SET_PWM SET_ANALOG
10123 | Postheat_1 |  | 0 - none 1 - electric 2 - water 3 - wco 4 - DX | 0 | 4 | 0 | NONE ELECTRIC WATER WCO DX
10124 | Postheat_set_2 |  | 0 - PWM (module B) 1 - analog | 0 | 1 | 0 | SET_PWM SET_ANALOG
10125 | Postheat_2 |  | 0 - none (module B) 1 - electric 2 - water 3 - wco 4 - DX | 0 | 4 | 0 | NONE ELECTRIC WATER WCO DX
10126 | HEPA_filter_used |  | 0 - non 1 - mount | 0 | 0 | 0 | HEPA_NON HEPA_MOUNT
10127 | reserva |  |  | 0 | 0 | 0
10128 | Recirculation |  | 0 - non 1 - mount | 0 | 0 | 0 | RECIRCULATION_NON MOUNT
10129 | Bypass |  | 0 - non 1 - stepless 0 - 10V 2 - OPEN/CLOSE | 0 | 2 | 1 | BYPASS_NON STEPLESS_10V OPEN_CLOSE
10130 | RecupType |  | 0 - non 1 - plate exchanger 2 - rotary wheel 3 - enthalpy plate | 0 | 3 | 1 | RECUPTYPE_NON PLATE EXCHANGER ROTARY WHEEL ENTHALPY PLATE
10131 | ADBmodule |  | 0 - non 1 - internal 2 - external | 0 | 2 | 0 | ADBMODUL_NON INTERNAL EXTERNAL
10132 | MotorType |  | 0 - EC 1 - AC 2 - DC | 0 | 2 | 0 | MOTORTYPE_EC MOTORTYPE_AC MOTORTYPE_DC
10133 | MotorSpecific |  | 0 - EBM 1 - FansTech | 0 | 1 | 0 | EBM FANSTECH
10134 | MotorEC_set |  | 0 - PWM 1 - analog (0-10V) | 0 | 1 | 0 | EC_PWM EC_ANALOG
10135 | SensorFilterIn |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10136 | SensorFilterOut |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10137 | SensorFanInlet |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10138 | SensorFanOut |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10139 | SensorDuct |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10140 | SensorC4 |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10141 | SensorRH |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10142 | SensorRHRec |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10143 | SensorAQS |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10144 | TempEXT1 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10145 | TempEXT2 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10146 | TempEXT3 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10147 | TempEXT4 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10148 | TempINT0 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10149 | TempINT1 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10150 | TempINT2 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10151 | TempWIn |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10152 | TempWOut |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10153 | TempRoom |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10154 | HeaterAlarm1 |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10155 | HeaterAlarm2 |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10156 | Inlet_fan |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10157 | Outlet_fan |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10158 | A_module |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10159 | G_module |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10160 | Xxx_module |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10161 | Room BMS |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10162 | EXT1 BMS |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10163 | FilterDisableStatus |  | 0 - FILTER_ALL_ACTIVE 1 -FILTER_DISABLE_INLET 2 - FILTER_DISABLE_OUTLET | 0 | 2 | 0
10164 | Reserva |  |  | 0 | 0 | 0

## SERVICE
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Service register (Factory reset set to default)
20001 | HighCO2Level1100 |  | 350 - 1100ppm | 350 | 1100 | 1100
20002 | LowCO2Level1100 |  | 350 - 1100ppm | 350 | 1100 | 350
20003 | HighCO2Level2000 |  | 350 - 2000ppm | 350 | 2000 | 2000
20004 | LowCO2Level2000 |  | 350 - 2000ppm | 350 | 2000 | 350
20005 | HighAQSLevelUni |  | % | 0 | 100 | 100
20006 | LowAQSLevelUni |  | % | 0 | 100 | 0
20007 | FlowOfset |  | % | -100 | 50 | 0
20008 | Reserva |  |  | 0 | 0 | 0
20009 | NoBodyTimeOut |  | min | 1 | 60 | 30
20010 | NobodyFlow |  | % | 20 | 50 | 20
20011 | BoostFromOff |  | 0 - Boost from run (only) 1 - Boost from off | 0 | 1 | 0 | BOOST_FROM_RUN BOOST_FROM_OFF
20012 | BoostTimer |  | min | 1 | 60 | 3
20013 | BoostFlow |  | % | 0 | 100 | 100
20014 | FreecoolingEnable |  | 0 - disable 1 - enable | 0 | 1 | 0 | FREECOOL_DISABLE FREECOOL_ENABLE
20015 | FreecoolingAirFlow |  | % | 50 | 100 | 100
20016 | FreecoolingTempEU |  | °C (°F) | 12(53,6) | 25(77) | 20
20017 | FreecoolingOnMonth |  | Month for start freecooling season | 1 | 12 | 6
20018 | FreecoolingOnDay |  | Day for start freecooling season | 1 | 31 | 1
20019 | FreecoolingOnHour |  | Hour for start freecooling | 0 | 23 | 20
20020 | FreecoolingOnMin |  | Min for start freecooling | 0 | 59 | 0
20021 | FreecoolingOffMonth |  | Month for stop freecooling season | 1 | 12 | 9
20022 | FreecoolingOffDay |  | Day for stop freecooling season | 1 | 31 | 1
20023 | FreecoolingOffHour |  | Hour for stop freecooling | 0 | 23 | 6
20024 | FreecoolingOffmin |  | Min for stop freecooling | 0 | 59 | 0
20025 | PID_Postheater1_Proportional range |  | PID_Pxx °C (°F) | 5(41) | 60(140) | 20(68)
20026 | PID_Postheater1_Integration constant |  | PID_xIx (sec) | 1 | 255 | 60
20027 | PID_Postheater1_derivative constant |  | PID_xxD (min) | 0 | 10 | 0
20028 | PID_Postheater2_Proportional range |  | PID_Pxx °C (°F) | 5(41) | 60(140) | 20(68)
20029 | PID_Postheater2_Integration constant |  | PID_xIx (sec) | 1 | 255 | 60
20030 | PID_Postheater2_derivative constant |  | PID_xxD (min) | 0 | 10 | 0
20031 | PID_Peheater_Proportional range |  | PID_Pxx °C (°F) | 5(41) | 60(140) | 20(68)
20032 | PID_Preheater_Integration constant |  | PID_xIx (sec) | 1 | 255 | 60
20033 | PID_Preheater_derivative constant |  | PID_xxD (min) | 0 | 10 | 0
20034 | SupplyDuctTempMax |  | Maximal supply duct temperature °C (°F) | 25(77) | 45(113) | 30(86)
20035 | SupplyDuctTempMin |  | Minimal supply duct temperature °C (°F) | 15(59) | 20(68) | 15(59)
20036 | RequiredPressureVAV |  | Pa | 0 | 1000 | 30
20037 | BypassTemperature |  | Minimal bypass temperature | 0(32) | 20(68) | 15(59)
20038 | MaxFlowCalibration |  | Maximal flow after calibration | 0 | 15000 | dle adresy 10114 nebo 10111
20039 | MaxPressureCalibration |  | Maximal pressure after calibration | 0 | 5000 | 30
20040 | FanCalibrationProcessed |  | FanCalibrationSucessfullyTerminated | 0 | 1 | 0 | FAN_CALIBRATION_NONE FAN_CALIBRATION_PROCESSED
20041 | FilterCalibrationProcessed |  | FilterCalibrationSucessfullyTerminated | 0 | 1 | 0 | FILTER_CALIBRATION_NONE FILTER_CALIBRATION_PROCESSED
20042 | reserva |  |  | 0 | 0 | 0
20043 | reserva |  |  | 0 | 0 | 0
20044 | OutsideTempSensorBMS |  | Outside temerature from BMS enable | 0 | 1 | 0 | OUT_TEMP-BMS_ENABLE OUT_TEMP_BMS_DISABLE
20045 | FlowReductionUnderDuctMin |  | 0 - disable 1 - enable | 0 | 1 | 1 | DUCT_MIN_FLOW_REDUCTION_DISABLE DUCT_MIN_FLOW_REDUCTION_ENABLE
20046 | Rec_CO2Level1100 |  | 350 - 1100ppm | 350 | 1100 | 1000
20047 | Rec_CO2Level2000 |  | 350 - 2000ppm | 350 | 2000 | 1000
20048 | Rec_Temp_setpoint |  | °C (°F) | 25(77) | 40(104) | 30(86)
20049 | Rec_Temp_setpoint_winter |  | °C (°F) | -20(-4) | -5(23) | -10(14)
20050 | Rec_PID_P |  | PID_Pxx % | 5 | 70 | 20
20051 | Rec_PID_I |  | PID_xIx (sec) | 1 | 255 | 60
20052 | Rec_PID_D |  | PID_xxD (min) | 0 | 10 | 0
AIR CURTAIN
20053 | SummerHeatEnable |  | Enable summer heat blocation | 0 | 1 | 0
20054 | WinterMounthStart |  | Mounth when winter starts | 1 | 12 | 10
20055 | WinterMounthStop |  | Mounth when winter ends | 1 | 12 | 4
20056 | SummerTempHeaterEnable |  | Limit temperature to enable heat in summer | 10 | 20 | 15
20057 | AutoSpeedControlEnable |  | Enable automatic speed control use 0 - disable 1 - enable | 0 | 1 | 0
20058 | AutoSpeedControlDeltaT |  | Delta T for automatic speed control changes (setpoint vs outside temperature) | 1 | 5 | 1
20059 | NightTempReductionEnable |  | NightTempReductionEnable | 0 | 1 | 0
20060 | NightTempReductionSetpointShift |  | Temperature setpoint shift for night reduction | 1 | 5 | 3
20061 | NightStartHour |  | Definition when night time start (hour) | 0 | 23 | 0
20062 | NightStartMinute |  | Definition when night time ends (hour) | 0 | 59 | 0
20063 | NightStopHour |  | Definition when night time start (hour) | 0 | 23 | 0
20064 | NightStopMinute |  | Definition when night time ends (hour) | 0 | 59 | 0
20065 | DoorContactEnable |  | Door contact enable to use 0 - disable 1 - enable | 0 | 1 | 1
20066 | DoorContactMode |  | Door contact mode selection 0 - Fixed 1 - Selflearning | 0 | 1 | 0
20067 | DoorContactFixedFlow_open |  | Air flow in ‰ for Fixed door Range set according (FACTORY SET: 10102 and 10111 …10116) | - | - | 200
20068 | DoorContactFixedHeat_open |  | Heat output for fixed door | 0 | 100 | 0
20069 | DoorContactFixedTempSetpoint |  | Setpoint temperature for Fixed door Range set according selected sensor: Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | - | 15
20070 | DoorContactFixedOverRunEnable |  | Overrun mode 0 - disable 1 - time interval 2 - temperature | 0 | 2 | 1
20071 | DoorContactFixedOverRunMinflowTime |  | Overrun time on minimal speed 5 - 300sec | 5 | 300 | 10
20072 | DoorContactFixedOverRunMaxflowTime |  | Overrun time on maximal speed 5 - 300sec | 5 | 300 | 10
20073 | DoorContactFixedOverRunTempSetpoint |  | Setpoint temperature for overrun to temperature Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | - | 15
20074 | DoorContactFixedOverRunTempSelect |  | Overrun temperature sensor selection 0 - Sensor CT-ROOM 1 - Thermostat | 0 | 1 | 0

## SERVICE HARD
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Service register (Factory reset no effect)
25000 | VentilationMode |  | 0 - Manual 1 - DCV 2 - CAV 3 - VAV 4 - VAVC4 5 - PCO | 0 | 5 | 0 | MANUAL DCV CAV VAV VAVC4
25001 | Water_antifreeze_outlet_fan |  | 0 - disable 1 - enable | 0 | 1 | 0 | WAOF_DISABLE WAOF_ENABLE
25002 | RecirculationMode |  | 0 - Disable 1 - Air Quality Sensor 2000 2 - Air Quality Sensor 1100 3 - Temperature | 0 | 3 | 0 | RECIRC_AQS RECIRC_TEMP
25003 | AQS sensor selection |  | 0 - non 1 - CO2 2000ppm 2 - CO2 1100ppm 3 - RH 4 - VOC 5 - External control 0 - 10V | 0 | 5 | 0 | AQS_NON AQS_CO2_2000 AQS_CO2_1100 AQS_RH AQS_VOC AQS_UNI_0_10V
25004 | ADB_external |  | 0 - disable 1 - enable | 0 | 1 | 0 | RECIRC_ENABLE RECIRC_DISABLE
25005 | Postheat_2_external |  | ALWAYS ANANLOG 0 - none (module B) 1 - electric 2 - water 3 - wco 4 - DX | 0 | 4 | 0 | NONE ELECTRIC WATER WCO DX
25006 | Recirculation_external |  | 0 - disable 1 - enable | 0 | 1 | 0 | RECIRC_ENABLE RECIRC_DISABLE
25007 | Preheater_2_external |  | ALWAYS ANALOG 0 - none 1 - electric 2 - water | 0 | 2 | 0 | PRE_NON PRE_ELECTRIC PRE_WATER
25008 | HwSettings |  | 0 - DI-4.x = FIRE 1 - DI-4.x = NONOCCUPIED | 0 | 1 | 1 | DI_4_1_FIRE DI_4_1_NOBODY
25009 | TempSensorSelection |  | 0 - Supply duct (15-45°C; 59-113F) 1 - Extract duct (15-30°C; 59-86F) 2 - Room (15-30°C; 59-86F) 3 - Thermostat 4 - Room BMS | 0 | 2 | 0 | T_SUPPLY_DUCT T_EXTRACT_DUCT T_ROOM
25010 | MinimalPowerDX |  | % | 10 | 100 | 40
25011 | DeadBandDX |  | mV | 100 | 2000 | 1000
25012 | MaxStartsPerHourDX |  | x-times/hour | 3 | 60 | 6
25013 | HeatCoolTimeOut |  | Heat/Cool timeout (min) | 1 | 20 | 3
25014 | DxControlSignal |  | 0 - 0-10V 1 - ON/OFF 2 - OFF/ON 3 - 0-10V-ON/OFF 4 - 0-10V-OFF/ON 5 - 0-10V-ON/OFF - inverted chiller 6 - 0-10V-OFF/ON - inverted chiller | 0 | 6 | 0 | DX_CTRL_SIGNAL_0_10V DX_CTRL_SIGNAL_ON_OFF DX_CTRL_SIGNAL_OFF_ON DX_CTRL_SIGNAL_0_10V_ON_OFF DX_CTRL_SIGNAL_0_10V_OFF_ON DX_CTRL_SIGNAL_0_10V_ON_OFF_INV_CHILLER DX_CTRL_SIGNAL_0_10V_OFF_ON_INV_CHILLER
25015 | LogicDxErrorContact |  | 0 - connected = error 1 - connected = OK | 0 | 1 | 1 | DX_ERROR_CONNECTED DX_OK_ERROR_CONNECTED
25016 | LogicDxDefrost |  | 0 - connected = defrost 1 - connected = OK | 0 | 1 | 1 | DX_DEFROST_CONNECTED DX_OK_DEFROST_CONNECTED
25017 | LogicDxHeatCoolSwitch |  | 0 - connected = cooling 1 - connected = heating | 0 | 1 | 1 | DX_HEAT_CONNECTED DX_COOL_CONNECTED
25018 | LogicRunOutput |  | 0 - connected = stop 1 - connected = RUN | 0 | 1 | 0 | RUN_CONNECTED_STOP RUN_CONNECTED_RUN
25019 | FilterWoringHours |  | Filter working hous en./deactivate | 0 | 1 | 0
25020 | FilterMaxHours |  | Maximal filter working hours | 200 | 3000 | 1440
25021 | modbus addres |  |  | 1 | 247 | 1
25022 | modbus baudrate |  | 4800 9600 14400 19200 38400 | 4800 | 38400 | 9600
25023 | modbus parity |  | NONE ODD EVEN | 0 | 2 | 1
25024 | AQS placement |  | MASTER SLAVE | 0 | 1 | 0
25025 | Slave present |  | 0 - non 1 - used | 0 | 1 | 0
25026 | PCO_dpress |  |  | -250 | 250 | 0
25027 | DCV_breating |  | 0 - non 1 - used | 0 | 1 | 0
25028 | HEPA_filter |  | 0 - non 1 - used | 0 | 1 | 0
25029 | Daylight_saving |  | 0 - NONE 1 - USED | 0 | 1 | 1
25030 | FireMode |  | FIRE_MODE_OFF FIRE_MODE_ALL_FAN FIRE_MODE_SUPPLY FIRE_MODE_RETURN | 0 | 3 | 2
25031 | FireFlow |  |  | 0 | 100
AIR CURTAIN
25032 | OutsideTempSensorAirCurtain |  | Outside temerature from BMS enable | 0 | 2 | 0 | OUT_TEMP_DISABLE = 0, OUT_TEMP_EXT1, OUT_TEMP_BMS
25033 | TemperatureControlMode |  | 0 - manual 1 - automatic | 0 | 1 | 0
25034 | ErrorLogic |  | 0 - NC 1 - NO | 0 | 1 | 1
25035 | DoorContactLogic |  | 0 - NC 1 - NO | 0 | 1 | 1
25036 | ExtCtrlLogic |  | 0 - NC 1 - NO | 0 | 1 | 0
25037 | RoomThermLogic |  | 0 - NC 1 - NO | 0 | 1 | 0
25038 | ExtCtrlFunction |  | 0 - DI-5.x = NOT USED 1 - DI-5.x = External control 2 - DI-5.x = Night reduction | 0 | 2 | 0
25039 | AntifreezeTempAirSet |  | Antifreeze air temperature (INT-1) | 5 | 15 | 5
25040 | AntifreezeTempWoutSet |  | Antifreeze water return temperature | 10 | 20 | 10
25041 | AntifreezeTempDxSet |  | Antifreeze fluid temperature | 0 | 5 | 0
25042 | NumberOfSlaveUnit |  | Specified number of slave units | 0 | 10 | 0
25043 | GlobalDoorContactEnable |  | Door contact shared from master | 0 | 1 | 1
25044 | GlobalExtCtrlEnable |  | External control shared from master | 0 | 1 | 1
25045 | LocalSlavePowerSwitchEnable |  | 0 - disable 1 - enable | 0 | 1 | 0
25046 | PreferManualOutput |  | 0 - digital 1 - analog | 0 | 1 | 0
25047 | NumOfDigitalHeaters |  |  | 0 | 1 | 1
25048 | NumOfMotors |  |  | 0 | 8 | 0
AHU
25049 | NumOfHeaterSection |  | 0 - 1 Section 1 - 2 Sections 2 - 3 Sections | 0 | 2 | 0
25050 | NumberOfSensors |  | IBUS Gateway | 0 | 24 | 0
25051 | modbus baudrate |  | IBUS Gateway | 0 | 4 | 0
25052 | modbus parity |  | IBUS Gateway | 0 | 2 | 1
25053 | Reserva1 |  |  | 0 | 0 | 0
25054 | Reserva2 |  |  | 0 | 0 | 0
25055 | IBUS Baudrate |  | 0 - 19200 1 - 9600 2 - 4800 | 0 | 2 | 0
25056 | AntiCovid_rotary wheel stop |  | 0 - rotary wheel - active 1 - rotary wheel - inactive | 0 | 1 | 0
25057 | Enable_Freecooling_RH |  | 0 - Freecooling RH - disable 1 - Freecooling RH - enabled | 0 | 1 | 0
25058 | Enable_Preheater_RH |  | 0 - Preheater RH - disable 1 - Preheater RH - enabled | 0 | 1 | 0
25059 | Enable_Efficiency_RH |  | 0 - Efficiency RH - disable 1 - Efficiency RH - enabled | 0 | 1 | 0
25060 | Freecooling_RH_DewPointMax |  | Freecooling RH setpoint | 0(32) | 15(60) | 0(32)
25061 | Savana_ExhaustFan |  |  | 0 | 100 | 0

## INFO
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Info register - read only (Factory reset no effect)
16000 | Jumper1 |  | 0 - non 1 - fitted | 0 | 1 | - | NON FITTED
16001 | Jumper2 |  | 0 - non 1 - fitted | 0 | 1 | - | NON FITTED
16002 | Jumper2 |  | 0 - non 1 - fitted | 0 | 1 | - | NON FITTED
16003 | ActualCurrent |  | mA | 0 | 0xFFFF | -
16004 | ActualVoltage |  | V | 0 | 0xFFFF | -
16005 | ActualPower |  | W | 0 | 0xFFFF | -
16006 | TotalConsumption_L |  | kW/h | 0 | 0xFFFF | -
16007 | TotalConsumption_H |  |  | 0 | 0xFFFF | -
16008 | IP adress 0.x.x.x |  | IP adress part1 (0x00-0xFF) | 0 | 255 | 192
16009 | IP adress x.0.x.x |  | IP adress part2 (0x00-0xFF) | 0 | 255 | 168
16010 | IP adress x.x.0.x |  | IP adress part3 (0x00-0xFF) | 0 | 255 | 0
16011 | IP adress x.x.x.0 |  | IP adress part4 (0x00-0xFF) | 0 | 255 | 100
16012 | Mask 0.x.x.x |  | Mask part1 (0x00-0xFF) | 0 | 255 | 255
16013 | Mask x.0.x.x |  | Mask part2 (0x00-0xFF) | 0 | 255 | 255
16014 | Mask x.x.0.x |  | Mask part3 (0x00-0xFF) | 0 | 255 | 255
16015 | Mask x.x.x.0 |  | Mask part4 (0x00-0xFF) | 0 | 255 | 0
16016 | Gateway 0.x.x.x |  | Gateway part1 (0x00-0xFF) | 0 | 255 | 192
16017 | Gateway x.0.x.x |  | Gateway part2 (0x00-0xFF) | 0 | 255 | 168
16018 | Gateway x.x.0.x |  | Gateway part3 (0x00-0xFF) | 0 | 255 | 0
16019 | Gateway x.x.x.0 |  | Gateway part4 (0x00-0xFF) | 0 | 255 | 1
16020 | DHCP |  | 0 - DHCP off 1 - DHCP on | 0 | 1 | 0 | DHCP_OFF DHCP_ON
16021 | ModbusPort |  | Port number 1 - 0xFFFF | 1 | 0xFFFF | 502
16022 | MAC adress 0.x.x.x.x.x |  | MAC adress part1 | 0 | 255 | -
16023 | MAC adress x.0.x.x.x.x |  | MAC adress part2 | 0 | 255 | -
16024 | MAC adress x.x.0.x.x.x |  | MAC adress part3 | 0 | 255 | -
16025 | MAC adress x.x.x.0.x.x |  | MAC adress part4 | 0 | 255 | -
16026 | MAC adress x.x.x.x.0.x |  | MAC adress part5 | 0 | 255 | -
16027 | MAC adress x.x.x.x.x.0 |  | MAC adress part6 | 0 | 255 | -
16028 | HW version Module A |  |  | 0 | FFFF
16029 | FW Module A |  | Firmware version Module A | 0 | FFFF
16030 | FW Module B |  | Firmware version Module B | 0 | FFFF
16031 | FW Module C1 |  | Firmware version Module C1 | 0 | FFFF
16032 | FW Module C2 |  | Firmware version Module C2 | 0 | FFFF
16033 | FW Module C3 |  | Firmware version Module C3 | 0 | FFFF
16034 | FW Module C4 |  | Firmware version Module C4 | 0 | FFFF
16035 | FW Module C5 |  | Firmware version Module C5 | 0 | FFFF
16036 | FW Module C6 |  | Firmware version Module C6 | 0 | FFFF
16037 | FW Module C7 |  | Firmware version Module C7 | 0 | FFFF
16038 | FW Module C8 |  | Firmware version Module C8 | 0 | FFFF
16039 | FW Module C9 |  | Firmware version Module C9 | 0 | FFFF
16040 | FW Module C10 |  | Firmware version Module C10 | 0 | FFFF
16041 | FW Module G |  | Firmware version Module G | 0 | FFFF
16042 | Bootloader FW |  | Firmware version bootloader | 0 | FFFF
16043 | FW Module K |  | Firmware version Module K | 0 | FFFF
16044 | BTCP_1 |  | Firmware version bootloader CP | 0 | FFFF
16045 | FWCP_1 |  | Firmware version CP | 0 | FFFF
16046 | BTCP_2 |  | Firmware version bootloader CP | 0 | FFFF
16047 | FWCP_2 |  | Firmware version CP | 0 | FFFF
16048 | BTCP_3 |  | Firmware version bootloader CP | 0 | FFFF
16049 | FWCP_3 |  | Firmware version CP | 0 | FFFF
16050 | FW Module L1 |  | Firmware version Module L1 | 0 | FFFF
16051 | FW Module L2 |  | Firmware version Module L2 | 0 | FFFF
16052 | FW Module L3 |  | Firmware version Module L3 | 0 | FFFF
16053 | FW Module L4 |  | Firmware version Module L4 | 0 | FFFF
16054 | FW Module L5 |  | Firmware version Module L5 | 0 | FFFF
16055 | FW Module L6 |  | Firmware version Module L6 | 0 | FFFF
16056 | FW Module L7 |  | Firmware version Module L7 | 0 | FFFF
16057 | FW Module L8 |  | Firmware version Module L8 | 0 | FFFF
16058 | FW Module L9 |  | Firmware version Module L9 | 0 | FFFF
16059 | FW Module L10 |  | Firmware version Module L10 | 0 | FFFF
16060 | passmode_1
16061 | passmode_2
16062 | passmode_2
16063 | DHCP server |  | 0 - DHCP off 1 - DHCP on | 0 | 1 | 0
16064 | BACnet port |  |  | 1 | 0xFFFF | 0xBAC0
16065 | BACnet device ID MSB |  |  | 0 | 0xFFFF | 0
16066 | BACnet device ID LSB |  |  | 0 | 0xFFFF | 1
16067 | Local Broadcast 0.x.x.x |  | IP adress part1 (0x00-0xFF) | 0 | 255 | 192
16068 | Local Broadcast x.0.x.x |  | IP adress part2 (0x00-0xFF) | 0 | 255 | 168
16069 | Local Broadcast x.x.0.x |  | IP adress part3 (0x00-0xFF) | 0 | 255 | 0
16070 | Local Broadcast x.x.x.0 |  | IP adress part4 (0x00-0xFF) | 0 | 255 | 255
16071 | Relay error extend
16072 | App pin
Note on H6: Only with ModuleEnergyMeasure

## STATUS_AHU
Address | Name | Structure | Info | Min. Value | Max. Value | Enum
Status regiSter - read only (Factory reset no effect)
Unit global status1
15000 | bit0 |  | ON/OFF | 0 | 1 | ON OFF
| bit1 |  | MANUAL | 0 | 1 | MANUAL_NON MANUAL_MODE
| bit2 |  | CAV | 0 | 0 | CAV_NON CAV_MODE
| bit3 |  | VAV | 0 | 0 | VAV_NON VAV_MODE
| bit4 |  | DCV | 0 | 1 | DCV_NON DCV_MODE
| bit5 |  | Fire | 0 | 1 | FIRE_NON FIRE_MODE
| bit6 |  | Boost | 0 | 1 | BOOST_NON BOOST_MODE
| bit7 |  | Nobody (Nonoccupied) | 0 | 1 | NOBODY_NON NOBODY_MODE
| bit8 |  | Freecooling | 0 | 1 | FRCOOL_NON FRCOOL_MODE
| bit9 |  | Timeswitch | 0 | 1 | TIME_SW_NON TIME_SW_MODE
| bit10 |  | Calibration | 0 | 1 | CALIBR_NON CALIBR_MODE
| bit11 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit12 |  | DirectControl | 0 | 1 | DIR_CTRL_NON DIR_CTRL_MODE
| bit13 |  | FilterInfo | 0 | 1
| bit14 |  | FW update error | 0 | 1
| bit15 |  | FW update active | 0 | 1
Unit global status2
15001 | bit0 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit1 |  | WaterHeater waiting for hot water | 0 | 1 | HOT_WATER_NON HOT_WATER
| bit2 |  | WaterHeater waiting for supply air temperature | 0 | 1 | AIR_TEMP_NO_OK AIR_TEMP_OK
| bit3 |  | WCO searching inlet water temp (cold/hot) | 0 | 1 | WATER_CHECK_ON WATER_CHECK_OFF
| bit4 |  | Recirculation | 0 | 1 | RECIRCULATION NO_RECIRCULATION
| bit5 |  | Simulation | 0 | 1 | SIMULATION NO_SIMULATION
| bit6 |  | Prefreecooling | 0 | 1 | PREFREECOOLING NO_PREFREECOOLING
| bit7 |  | Temp Flow Reduction | 0 | 1
| bit8 |  | PassiveHouseRestriction | 0 | 1
| bit9 |  | AdbActive | 0 | 1
| bit10 |  | VAVC4 | 0 | 1
| bit11 |  | PCO | 0 | 1
Software error1
15002 | bit0 |  | SwFanInletError | 0 | 1
| bit1 |  | SwFanOutletError | 0 | 1
| bit2 |  | SwFilterInletError | 0 | 1
| bit3 |  | SwFilterOutletError | 0 | 1
| bit4 |  | SwFilterInletWarning | 0 | 1
| bit5 |  | SwFilterOutletWarning | 0 | 1
| bit6 |  | SwPreheater1Error | 0 | 1
| bit7 |  | SwPostheater1Error | 0 | 1
| bit8 |  | SwPostheater2Error | 0 | 1
| bit9 |  | SwPreheater2Error | 0 | 1
| bit10 |  | SwAQS SensorError | 0 | 1
| bit11 |  | SwRotaryWheelError | 0 | 1
| bit12 |  | SwADBError | 0 | 1
| bit13 |  | SwDXError | 0 | 1
| bit14 |  | SwDXDefrost | 0 | 1
| bit15 |  | SwCondensateDrain | 0 | 1
Software error2
15003 | bit0 |  | SwGError | 0 | 1
| bit1 |  | SwGlobalError | 0 | 1
| bit2 |  | SwKError | 0 | 1
| bit3 |  | FilterInfo | 0 | 1
| bit4 |  | CfgFileError | 0 | 1
| bit5 |  | SwFilterHepaError | 0 | 1
| bit6 |  | SwFilterHepaWarning | 0 | 1
| bit7 |  | IBUSGatewayError | 0 | 1
Sensor status1
15004 | bit0 |  | TempEXT1St | 0 | 1 | OK ERROR
| bit1 |  | TempEXT2St | 0 | 1 | OK ERROR
| bit2 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit3 |  | TempEXT4St (module B) | 0 | 0 | OK ERROR
| bit4 |  | TempINT0St (module B) | 0 | 0 | OK ERROR
| bit5 |  | TempINT1St | 0 | 1 | OK ERROR
| bit6 |  | TempINT2St | 0 | 1 | OK ERROR
| bit7 |  | TempWInSt (module B) | 0 | 0 | OK ERROR
| bit8 |  | TempWOutSt (module B) | 0 | 0 | OK ERROR
| bit9 |  | TempRoomSt | 0 | 1 | OK ERROR
| bit10 |  | SensorFilterInSt | 0 | 0 | OK ERROR
| bit11 |  | SensorFilterOutSt | 0 | 0 | OK ERROR
| bit12 |  | SensorFanInletSt | 0 | 0 | OK ERROR
| bit13 |  | SensorFanOutSt | 0 | 0 | OK ERROR
| bit14 |  | SensorPressSt | 0 | 0 | OK ERROR
| bit15 |  | SensorFlowAlaramSt | 0 | 0 | OK ERROR
Sensor status2
15005 | bit0 |  | AqsSensorSt | 0 | 0 | OK ERROR
| bit1 |  | SensorRHRecSt | 0 | 0 | OK ERROR
| bit2 |  | OutsideTempSensorBmsSt | 0 | 0 | OK ERROR
| bit3 |  | SensorRHSt | 0 | 0 | OK ERROR
| bit4 |  | Sensor Filter HepaSt
| bit5 |  | SensorRH_E1St | 0 | 0 | OK ERROR
| bit6 |  | SensorRH_E2St | 0 | 0 | OK ERROR
| bit7 |  | SensorRH_I1St | 0 | 0 | OK ERROR
| bit8 |  | SensorRH_I2St | 0 | 0 | OK ERROR
Input Status1
15006 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 0 | OK ERROR
| bit1 |  | Status DI_2_SafetyTherm2 | 0 | 0 | OK ERROR
| bit2 |  | Status DI_3_Ext_Control | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Nobody (FIRE optional) | 0 | 1 | OK ERROR
| bit4 |  | Status DI_5_Boost | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_2 (Rotary wheel error) | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit9 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit10 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit11 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit12 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit13 |  | Status_DI_6_ADB_DX_error (module B) | 0 | 1 | OK ERROR
| bit14 |  | Status_DI_7_HeatPumpDefrost (module B) | 0 | 1 | OK ERROR
| bit15 |  | Status_DI_8_HeatPumpError (module B) | 0 | 1 | OK ERROR
Input Status2
15007 | bit0 |  | Status_DI_9_FIRE (module B) | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_10_CondensDrain (module B) | 0 | 1 | OK ERROR
Output Status1
15008 | bit0 |  | Status_DO_1_Flap_inlet | 0 | 1 | FLAP_CLOSED FLAP_OPEN
| bit1 |  | Status_DO_2_Flap_outlet | 0 | 1 | FLAP_CLOSED FLAP_OPEN
| bit2 |  | Status_DO_3_Run_indication | 0 | 1 | RUN_INDICATION NO_RUN
| bit3 |  | Status_DO_4_Water_pump | 0 | 1 | W_PUMP_A_ON W_PUMP_A_OFF
| bit4 |  | Status_DO_5_Heat_cool(module B) | 0 | 1 | EXCHANGER_COOL EXCHANGER_HEAT
| bit5 |  | Status_DO_6_Error | 0 | 1 | ERROR_B_OK ERROR_B_ERROR
| bit6 |  | Status_DO_7_ADB_on_off (module B) | 0 | 1 | ADB_ON ADB_OFF
| bit7 |  | Status_DO_8_HeatPump_on_off (module B) | 0 | 1 | HEAT_PUMP_ON HEAT_PUMP_OFF
| bit8 |  | Status_DO_9_WaterPump_on_off (module B) | 0 | 1 | W_PUMP_B_ON W_PUMP_B_OFF
Hardware Status1
15009 | bit0 |  | FRAM | 0 | 1
| bit1 |  | EEPROM | 0 | 1 | OK ERROR
| bit2 |  | Ethernet | 0 | 1 | OK ERROR
| bit3 |  | RTC_Cell | 0 | 1 | OK ERROR
| bit4 |  | MainPower | 0 | 1 | OK ERROR
| bit5 |  | ControlPanel | 0 | 1 | OK ERROR
| bit6 |  | B_module | 0 | 1 | OK ERROR
| bit7 |  | C_module_In_Press | 0 | 1 | OK ERROR
| bit8 |  | C_module_Out_Press | 0 | 1 | OK ERROR
| bit9 |  | C_module_In_Filter_Press | 0 | 1 | OK ERROR
| bit10 |  | C_module_Out_Filter_Press | 0 | 1 | OK ERROR
| bit11 |  | C_module_Duct_Press | 0 | 1 | OK ERROR
| bit12 |  | C_module_C4_Duct_Press | 0 | 1 | OK ERROR
| bit13 |  | C_module_RH | 0 | 1 | OK ERROR
| bit14 |  | AQS | 0 | 1 | OK ERROR
| bit15 |  | USB_over_current | 0 | 1 | OK ERROR
Hardware Status2
15010 | bit0 |  | Ethernet_communication | 0 | 1 | OK ERROR
| bit1 |  | C_module_Hepa_Press | 0 | 1 | OK ERROR
15011 | AirFlowInletFanDemand |  | m3/h (cfm) | 0 | 0xffff
15012 | AirFlowOutletFanDemand |  | m3/h (cfm) | 0 | 0xffff
15013 | AirFlowInletFanManual |  | ‰ of fan power | 0 | 1000
15014 | AirFlowOutletFanManual |  | ‰ of fan power | 0 | 1000
15015 | AirFlowInletFan |  | m3/h (cfm) | 0 | 0xffff
15016 | AirFlowOutletFan |  | m3/h (cfm) | 0 | 0xffff
15017 | TempEXT1 - outside air |  | °C (°F) x10 | -40 (-40) | 100 (212)
15018 | TempEXT2 - outside air after recuperatore before heater 1 |  | °C (°F) x10 | -40 (-40) | 100 (212)
15019 | TempEXT3 - outside air after heater 1 |  | °C (°F) x10 | -40 (-40) | 100 (212)
15020 | TempEXT4 - outside air after heater 2 |  | °C (°F) (module B) x10 | -40 (-40) | 100 (212)
15021 | TempINT0 |  | °C (°F) (module B) x10 | -40 (-40) | 100 (212)
15022 | TempINT1 - extract indoor air |  | °C (°F) x10 | -40 (-40) | 100 (212)
15023 | TempINT2 - extract indoor air after recuperator |  | °C (°F) x10 | -40 (-40) | 100 (212)
15024 | TempWIn |  | °C (°F) (module B) x10 | -40 (-40) | 100 (212)
15025 | TempWOut |  | °C (°F) (module B) x10 | -40 (-40) | 100 (212)
15026 | TempRoom |  | °C (°F) x10 | -40 (-40) | 100 (212)
15027 | SensorFilterIn |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15028 | SensorFilterOut |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15029 | SensorFanInlet |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15030 | SensorFanOut |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15031 | SensorPress |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15032 | SensorFlowAlarm |  |  | 0 | 1
15033 | AqsSensorValue |  | % | 0 | 100
15034 | SensorRHRec |  | % | 0 | 100
15035 | SensorRH |  | % (module C) | 0 | 100
15036 | PowerPreheater1 |  | % | 0 | 100
15037 | PowerPreheater2 |  | % (module B) | 0 | 100
15038 | PowerPostheater1 |  | % | 0 | 100
15039 | PowerPostheater2 |  | % (module B) | 0 | 100
15040 | PowerPostheater3 |  | % (module B) | 0 | 100
15041 | BypassPossition |  | % | 0 | 100
15042 | Recirculation |  | % (module B) | 0 | 100
15043 | TempOutsideBMS |  | °C (°F) x10 | -40 (-40) | 100 (212)
15044 | InletFilterPercent |  | % | 0 | 100
15045 | OutletFilterPercent |  | % | 0 | 100
15046 | dummy |  |  | 0 | 0xFFFF
15047 | SensorFilterhEPA |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15048 | HepaFilterPercent |  | % | 0 | 100
15049 | Temperature setpoint |  | °C (°F) | -40 (-40) | 100 (212)
15050 | Efficiency_Rec_RH |  | % | -100 | 100
15051 | SensorRH_EXT1 |  | °C (°F) x10 | -40 (-40) | 100 (212)
15052 | SensorRH_EXT1_RH |  | % | 0 | 100
15053 | SensorRH_EXT2 |  | °C (°F) x10 | -40 (-40) | 100 (212)
15054 | SensorRH_EXT2_RH |  | % | 0 | 100
15055 | SensorRH_INT1 |  | °C (°F) x10 | -40 (-40) | 100 (212)
15056 | SensorRH_INT1_RH |  | % | 0 | 100
15057 | SensorRH_INT2 |  | °C (°F) x10 | -40 (-40) | 100 (212)
15058 | SensorRH_INT2_RH |  | % | 0 | 100

## STATUS_AC
Address | Name | Structure | Info | Min. Value | Max. Value | Enum
Status regiSter - read only (Factory reset no effect)
Unit global status
18000 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Automatic heat | 0 | 1 | AUTOHEAT_NON AUTOHEAT_MODE
| bit2 |  | Automatic flow | 0 | 1 | AUTOFLOW_NON AUTOFLOW_MODE
| bit3 |  | NightReduction | 0 | 1 | NIGHTREDUCTION_NON NIGHTREDUCTION_MODE
| bit4 |  | Timeswitch | 0 | 1 | TIME_SW_NON TIME_SW_MODE
| bit5 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit6 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit7 |  | WaterHeater waiting for hot water | 0 | 1 | HOT_WATER_NON HOT_WATER
| bit8 |  | SummerHeat | 0 | 1 | WINTER SUMMER
| bit9 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit10 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit11 |  | Heater Under Power | 0 | 1
| bit12 |  | Savana Day Night | 0 | 1 | SAVANA_DAY SAVANA_NIGHT
| bit13 |  | reserva | 0 | 0
| bit14 |  | FW update error | 0 | 1
| bit15 |  | FW update active | 0 | 1
Software error
18001 | bit0 |  | SwFanError | 0 | 1
| bit1 |  | SwFanError1 | 0 | 1
| bit2 |  | SwFilterError | 0 | 1
| bit3 |  | SwFilterWarning | 0 | 1
| bit4 |  | SwHeaterError | 0 | 1
| bit5 |  | SwDXError | 0 | 1
| bit6 |  | SwDXDefrost | 0 | 1
| bit7 |  | SwGlobalError | 0 | 1
| bit8 |  | CfgFileError | 0 | 1
| bit9 |  | IBUSGatewayError | 0 | 1
| bit10 |  | Alarm temp room | 0 | 1
| bit11 |  | AtFreeze_cnt_overflow | 0 | 1
Software error 1
18002 | reserva
Sensor status
18003 | bit0 |  | TempEXT1St - Outside air | 0 | 1 | OK ERROR
| bit1 |  | TempEXT3St - Outlet air | 0 | 1 | OK ERROR
| bit2 |  | TempINT1St - Inlet air | 0 | 1 | OK ERROR
| bit3 |  | TempWOutSt - Water return | 0 | 1 | OK ERROR
| bit4 |  | TempRoomSt - Room | 0 | 1 | OK ERROR
| bit5 |  | OutsideTempSensorBmsSt | 0 | 1 | OK ERROR
| bit6 |  | RoomTempSensorBmsSt | 0 | 1 | OK ERROR
| bit7 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
Input Status
18004 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 0 | OK ERROR
| bit1 |  | Status DI_2_SafetyTherm2 | 0 | 0 | OK ERROR
| bit2 |  | Status DI_3_Ext_Control | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_RoomThermostat | 0 | 1 | OK ERROR
| bit4 |  | Status DI_5_Door | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit9 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit10 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit11 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit12 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit13 |  | Status_DI_6_ADB_DX_error | 0 | 1 | OK ERROR
| bit14 |  | Status_DI_7_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit15 |  | Status_DI_8_HeatPumpError | 0 | 1 | OK ERROR
Output Status
18005 | bit0 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit1 |  | Status_DO_1_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit2 |  | Status_DO_3_Run_indication | 0 | 1 | RUN_INDICATION NO_RUN
| bit3 |  | Status_DO_4_Error | 0 | 1 | ERROR_INDICATION NO_ERROR
| bit4 |  | Status_DO_5_Heat_cool | 0 | 1 | EXCHANGER_COOL EXCHANGER_HEAT
| bit5 |  | Status_DO_6_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit6 |  | Damper | 0 | 1
18006 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
18007 | TempEXT1 - Outside air |  | °C (°F) x10 | -40 (-40) | 100 (212)
18008 | TempEXT3 - Outlet air |  | °C (°F) x10 | -40 (-40) | 100 (212)
18009 | TempINT1 - Inlet air |  | °C (°F) x10 | -40 (-40) | 100 (212)
18010 | TempWOut - Water return |  | °C (°F) x10 | -40 (-40) | 100 (212)
18011 | TempRoom - Room |  | °C (°F) x10 | -40 (-40) | 100 (212)
18012 | SensorFlowAlarm |  |  | 0 | 1
18013 | PowerHeater |  | % | 0 | 100
18014 | TempOutsideBMS |  | °C (°F) x10 | -40 (-40) | 100 (212)
18015 | RoomBMS |  | °C (°F) x10 | -40 (-40) | 101 (212)
18016 | FilterPercent |  | % | 0 | 100
18017 | dummy |  |  | 0 | 0xFFFF
Tacho Board Status
18018 | bit1 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit9 |  | Status_DI_TACHO_9 | 0 | 1 | OK ERROR
| bit10 |  | Status_DI_TACHO_10 | 0 | 1 | OK ERROR
18019 | Temperature Setpoint |  | °C (°F) | -40 (-40) | 100 (212)
18020 | Reserva

## SLAVE_AC_STATUS
Address | Name | Structure | Info | Min. Value | Max. Value | Enum
Status regiSter - read only (Factory reset no effect)
Slave 1
Unit global status
14000 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat | 0 | 1
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14001 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower | 0 | 1
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14002 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14003 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14004 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14005 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14006 | SensorFlowAlarm |  |  | 0 | 1
14007 | PowerHeater |  | % | 0 | 100
Tacho Board
14008 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14009 | Reserva 2
Slave 2
Unit global status
14010 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14011 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14012 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14013 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14014 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14015 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14016 | SensorFlowAlarm |  |  | 0 | 1
14017 | PowerHeater |  | % | 0 | 100
Tacho Board
140018 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
140019 | Reserva 2
Slave 3
Unit global status
14020 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14021 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14022 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14023 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14024 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14025 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14026 | SensorFlowAlarm |  |  | 0 | 1
14027 | PowerHeater |  | % | 0 | 100
Tacho Board
14028 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14029 | Reserva 2
Slave 4
Unit global status
14030 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14031 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14032 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14033 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14034 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14035 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14036 | SensorFlowAlarm |  |  | 0 | 1
14037 | PowerHeater |  | % | 0 | 100
Tacho Board
14038 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14039 | Reserva 2
Slave 5
Unit global status
14040 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14041 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14042 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14043 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14044 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14045 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14046 | SensorFlowAlarm |  |  | 0 | 1
14047 | PowerHeater |  | % | 0 | 100
Tacho Board
14048 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14049 | Reserva 2
Slave 6
Unit global status
14050 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14051 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14052 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14053 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14054 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14055 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14056 | SensorFlowAlarm |  |  | 0 | 1
14057 | PowerHeater |  | % | 0 | 100
Tacho Board
14058 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14059 | Reserva 2
Slave 7
Unit global status
14060 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14061 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14064 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14065 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14066 | SensorFlowAlarm |  |  | 0 | 1
14067 | PowerHeater |  | % | 0 | 100
Tacho Board
14068 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14069 | Reserva 2
Slave 8
Unit global status
14070 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14071 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14072 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14073 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14074 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14075 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14076 | SensorFlowAlarm |  |  | 0 | 1
14077 | PowerHeater |  | % | 0 | 100
Tacho Board
14078 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14079 | Reserva 2
Slave 9
Unit global status
14080 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14081 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14082 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14083 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14084 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14085 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14086 | SensorFlowAlarm |  |  | 0 | 1
14087 | PowerHeater |  | % | 0 | 100
Tacho Board
14088 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14089 | Reserva 2
Slave 10
Unit global status
14090 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14091 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
| bit12 |  | damper | 0 | 1
| bit13 |  | AtFreeze_cnt_overflow | 0 | 1
14092 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14093 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14094 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14095 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14096 | SensorFlowAlarm |  |  | 0 | 1
14097 | PowerHeater |  | % | 0 | 100
Tacho Board
14098 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14099 | Reserva 2

## SHARE
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Share register (Factory reset set to default)
21000 | Language |  | Language selection | 0 | 10 | 0 | ENGLISH - 0 FRENCH - 1 GERMAN - 2 RUSSIAN - 3 CZECH - 4 SPANISH - 5 PORTUGUESE - 6 ITALIAN - 7 SVENSKA - 8 SUOMI - 9
21001 | SwitchON |  | ON/OFF unit mode | 0 | 1 | 0 | OFF ON
21002 | AirFlowManual |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | - | -
21003 | Temperature |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE_HARD:25009): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-86F) Room (15-30°C; 59-86F) | - | - | -
21004 | TimeSwGlobalEnable |  | TimeSwitchGlobal enable/disable | 0 | 1 | 0 | TIMER_GLOBAL_DISABLE TIMER_GLOBAL_ENABLE
21005 | TimeSwMode |  | Active/Inactive timer mode (only read) | 0 | 1 | 0 | TIMER_MODE_OFF TIMER_MODE_ON
21006 | TimeSwFlow |  | only read
21007 | TimeSwTemp |  | only read
21008 | TimeSwOnOFF |  |  | 0 | 1 | 0 | TIMER_MODE_OFF TIMER_MODE_ON
21009 | BoostMode (AHU,HRU) Door contact (AC,IC) Day/Night (SC) |  | Activation of Boost mode For AC and IC - Door mode activation (SW activation) For SC - Day/Night switch | 0 | 1 | 0 | BOOST_OFF BOOST_ON
21010 | NoBodyMode |  | Nobody mode (Nonoccupied) activation/deactivation | 0 | 1 | 0 | NOBODY_OFF NOBOBY_ON
21011 | FreecoolingMode |  | Freecooling activation/deactivation | 0 | 1 | 0 | FREECOOL_OFF FREECOOL_ON
21012 | FanCalibration |  | FanCalibrationStart | 0 | 1 | 0 | FAN_CAL_OFF FAN_CAL_ON
21013 | FilterCalibration |  | FilterCalibrationStart | 0 | 1 | 0 | FIL_CAL_OFF FIL_CAL_ON
21014 | DirectControlMode |  | DirectControlMode activation | 0 | 1 | 0 | DIR_CTRL_ON DIR_CTRL_OFF
21015 | Recirculation |  | Recirculation enable | 0 | 1 | 0 | RECIRCL_OFF RECIRCL_ON
21016 | FilterClogedTimerReset |  | 0 - count 1 - timer reset | 0 | 1 | 0 | FILTER_TIMER_COUNT FILTER-TIMER_RESET
21017 | Pin1 |  | Setting data for CP only | 0 | 9 | 1
21018 | Pin2 |  | Setting data for CP only | 0 | 9 | 2
21019 | Pin3 |  | Setting data for CP only | 0 | 9 | 3
21020 | Pin4 |  | Setting data for CP only | 0 | 9 | 4
21021 | Pin_mode |  | Setting data for CP only | 0 | 1 | 0
21022 | CP_refresh_flag |  | Setting data for CP only | 0 | 1 | 1
21023 | Backlight_set |  | % Setting data for CP only | 40 | 100 | 100
AIR CURTAIN
21024 | ACR_ManualHeat |  | Heater power for manual mode | 0 | 100 | 0
21025 | TimeSwHeat |  |  | 0 | 100 | 0
SlaveSwitchOn
21026 | bit0 |  | Slave1 - off/on | 0 | 1 | 0
| bit1 |  | Slave2 - off/on | 0 | 1 | 0
| bit2 |  | Slave3 - off/on | 0 | 1 | 0
| bit3 |  | Slave4 - off/on | 0 | 1 | 0
| bit4 |  | Slave5 - off/on | 0 | 1 | 0
| bit5 |  | Slave6 - off/on | 0 | 1 | 0
| bit6 |  | Slave7 - off/on | 0 | 1 | 0
| bit7 |  | Slave8 - off/on | 0 | 1 | 0
| bit8 |  | Slave9 - off/on | 0 | 1 | 0
| bit9 |  | Slave10 - off/on | 0 | 1 | 0
| bit10 |  | Slave11 - off/on | 0 | 1 | 0
| bit11 |  | Slave12 - off/on | 0 | 1 | 0
| bit12 |  | Slave13 - off/on | 0 | 1 | 0
| bit13 |  | Slave14 - off/on | 0 | 1 | 0
| bit14 |  | Slave15 - off/on | 0 | 1 | 0
| bit15 |  | Slave16 - off/on | 0 | 1 | 0
21027 | Temperature Night |  |  | 5 | 30 | 15

## TIME
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Time register (Factory reset set to default)
17000 | ActualYear |  |  | 2000 | 2100
17001 | ActualMonth |  |  | 1 | 12
17002 | ActualDay |  |  | 1 | 31
17003 | ActualDayOfWeek |  |  | 1 | 7
17004 | ActualHour |  |  | 0 | 23
17005 | ActualMin |  |  | 0 | 59
17006 | ActualSec |  |  | 0 | 59

## TIME_DRIVER
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Time_driver register (Factory reset set to default)
17000 | SetYear |  |  | 2000 | 2100 | -
17001 | SetMonth |  |  | 1 | 12 | -
17002 | SetDay |  |  | 1 | 31 | -
17003 | SetDayOfWeek |  |  | 1 | 7 | -
17004 | SetHour |  |  | 0 | 23 | -
17005 | SetMin |  |  | 0 | 59 | -
17006 | SetSec |  |  | 0 | 59 | -
17007 | SetFlag |  |  | 0 | 1 | 0 |  | set time date to unit
17008 | ErrorLogNum |  |  | 1 | 20 | 1
17009 | ErrorLogClearFlag |  |  | 0 | 1 | 0

## TIME_SWITCH_WEEK
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Time_switch register (Factory reset set to default)
27000 | TimeSw_Monday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27001 | TimeSw_Monday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27002 | TimeSw_Monday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27003 | TimeSw_Monday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27004 | TimerSw_Monday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27005 | TimerSw_Monday_1_Heat |  | Only for AC | 0 | 100 | 0
27006 | TimeSw_Monday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27007 | TimeSw_Monday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27008 | TimeSw_Monday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27009 | TimeSw_Monday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27010 | TimerSw_Monday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27011 | TimerSw_Monday_2_Heat |  | Only for AC | 0 | 100 | 0
27012 | TimeSw_Monday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27013 | TimeSw_Monday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27014 | TimeSw_Monday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27015 | TimeSw_Monday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27016 | TimerSw_Monday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27017 | TimerSw_Monday_3_Heat |  | Only for AC | 0 | 100 | 0
27018 | TimeSw_Monday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27019 | TimeSw_Monday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27020 | TimeSw_Monday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27021 | TimeSw_Monday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27022 | TimerSw_Monday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27023 | TimerSw_Monday_4_Heat |  | Only for AC | 0 | 100 | 0
27024 | TimeSw_Monday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27025 | TimeSw_Monday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27026 | TimeSw_Monday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27027 | TimeSw_Monday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27028 | TimerSw_Monday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27029 | TimerSw_Monday_5_Heat |  | Only for AC | 0 | 100 | 0
27030 | TimeSw_Monday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27031 | TimeSw_Monday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27032 | TimeSw_Monday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27033 | TimeSw_Monday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27034 | TimerSw_Monday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27035 | TimerSw_Monday_6_Heat |  | Only for AC | 0 | 100 | 0
27036 | TimeSw_Monday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27037 | TimeSw_Monday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27038 | TimeSw_Monday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27039 | TimeSw_Monday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27040 | TimerSw_Monday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27041 | TimerSw_Monday_7_Heat |  | Only for AC | 0 | 100 | 0
27042 | TimeSw_Monday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27043 | TimeSw_Monday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27044 | TimeSw_Monday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27045 | TimeSw_Monday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27046 | TimerSw_Monday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27047 | TimerSw_Monday_8_Heat |  | Only for AC | 0 | 100 | 0
27048 | TimeSw_Tuesday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27049 | TimeSw_Tuesday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27050 | TimeSw_Tuesday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27051 | TimeSw_Tuesday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27052 | TimerSw_Tuesday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27053 | TimerSw_Tuesday_1_Heat |  | Only for AC | 0 | 100 | 0
27054 | TimeSw_Tuesday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27055 | TimeSw_Tuesday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27056 | TimeSw_Tuesday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27057 | TimeSw_Tuesday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27058 | TimerSw_Tuesday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27059 | TimerSw_Tuesday_2_Heat |  | Only for AC | 0 | 100 | 0
27060 | TimeSw_Tuesday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27061 | TimeSw_Tuesday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27062 | TimeSw_Tuesday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27063 | TimeSw_Tuesday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27064 | TimerSw_Tuesday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27065 | TimerSw_Tuesday_3_Heat |  | Only for AC | 0 | 100 | 0
27066 | TimeSw_Tuesday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27067 | TimeSw_Tuesday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27068 | TimeSw_Tuesday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27069 | TimeSw_Tuesday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27070 | TimerSw_Tuesday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27071 | TimerSw_Tuesday_4_Heat |  | Only for AC | 0 | 100 | 0
27072 | TimeSw_Tuesday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27073 | TimeSw_Tuesday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27074 | TimeSw_Tuesday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27075 | TimeSw_Tuesday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27076 | TimerSw_Tuesday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27077 | TimerSw_Tuesday_5_Heat |  | Only for AC | 0 | 100 | 0
27078 | TimeSw_Tuesday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27079 | TimeSw_Tuesday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27080 | TimeSw_Tuesday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27081 | TimeSw_Tuesday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27082 | TimerSw_Tuesday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27083 | TimerSw_Tuesday_6_Heat |  | Only for AC | 0 | 100 | 0
27084 | TimeSw_Tuesday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27085 | TimeSw_Tuesday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27086 | TimeSw_Tuesday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27087 | TimeSw_Tuesday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27088 | TimerSw_Tuesday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27089 | TimerSw_Tuesday_7_Heat |  | Only for AC | 0 | 100 | 0
27090 | TimeSw_Tuesday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27091 | TimeSw_Tuesday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27092 | TimeSw_Tuesday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27093 | TimeSw_Tuesday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27094 | TimerSw_Tuesday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27095 | TimerSw_Tuesday_8_Heat |  | Only for AC | 0 | 100 | 0
27096 | TimeSw_Wensday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27097 | TimeSw_Wensday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27098 | TimeSw_Wensday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27099 | TimeSw_Wensday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27100 | TimerSw_Wensday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27101 | TimerSw_Wensday_1_Heat |  | Only for AC | 0 | 100 | 0
27102 | TimeSw_Wensday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27103 | TimeSw_Wensday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27104 | TimeSw_Wensday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27105 | TimeSw_Wensday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27106 | TimerSw_Wensday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27107 | TimerSw_Wensday_2_Heat |  | Only for AC | 0 | 100 | 0
27108 | TimeSw_Wensday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27109 | TimeSw_Wensday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27110 | TimeSw_Wensday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27111 | TimeSw_Wensday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27112 | TimerSw_Wensday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27113 | TimerSw_Wensday_3_Heat |  | Only for AC | 0 | 100 | 0
27114 | TimeSw_Wensday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27115 | TimeSw_Wensday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27116 | TimeSw_Wensday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27117 | TimeSw_Wensday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27118 | TimerSw_Wensday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27119 | TimerSw_Wensday_4_Heat |  | Only for AC | 0 | 100 | 0
27120 | TimeSw_Wensday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27121 | TimeSw_Wensday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27122 | TimeSw_Wensday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27123 | TimeSw_Wensday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27124 | TimerSw_Wensday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27125 | TimerSw_Wensday_5_Heat |  | Only for AC | 0 | 100 | 0
27126 | TimeSw_Wensday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27127 | TimeSw_Wensday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27128 | TimeSw_Wensday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27129 | TimeSw_Wensday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27130 | TimerSw_Wensday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27131 | TimerSw_Wensday_6_Heat |  | Only for AC | 0 | 100 | 0
27132 | TimeSw_Wensday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27133 | TimeSw_Wensday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27134 | TimeSw_Wensday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27135 | TimeSw_Wensday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27136 | TimerSw_Wensday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27137 | TimerSw_Wensday_7_Heat |  | Only for AC | 0 | 100 | 0
27138 | TimeSw_Wensday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27139 | TimeSw_Wensday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27140 | TimeSw_Wensday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27141 | TimeSw_Wensday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27142 | TimerSw_Wensday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27143 | TimerSw_Wensday_8_Heat |  | Only for AC | 0 | 100 | 0
27144 | TimeSw_Thursday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27145 | TimeSw_Thursday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27146 | TimeSw_Thursday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27147 | TimeSw_Thursday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27148 | TimerSw_Thursday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27149 | TimerSw_Thursday_1_Heat |  | Only for AC | 0 | 100 | 0
27150 | TimeSw_Thursday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27151 | TimeSw_Thursday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27152 | TimeSw_Thursday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27153 | TimeSw_Thursday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27154 | TimerSw_Thursday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27155 | TimerSw_Thursday_2_Heat |  | Only for AC | 0 | 100 | 0
27156 | TimeSw_Thursday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27157 | TimeSw_Thursday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27158 | TimeSw_Thursday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27159 | TimeSw_Thursday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27160 | TimerSw_Thursday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27161 | TimerSw_Thursday_3_Heat |  | Only for AC | 0 | 100 | 0
27162 | TimeSw_Thursday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27163 | TimeSw_Thursday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27164 | TimeSw_Thursday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27165 | TimeSw_Thursday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27166 | TimerSw_Thursday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27167 | TimerSw_Thursday_4_Heat |  | Only for AC | 0 | 100 | 0
27168 | TimeSw_Thursday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27169 | TimeSw_Thursday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27170 | TimeSw_Thursday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27171 | TimeSw_Thursday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27172 | TimerSw_Thursday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27173 | TimerSw_Thursday_5_Heat |  | Only for AC | 0 | 100 | 0
27174 | TimeSw_Thursday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27175 | TimeSw_Thursday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27176 | TimeSw_Thursday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27177 | TimeSw_Thursday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27178 | TimerSw_Thursday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27179 | TimerSw_Thursday_6_Heat |  | Only for AC | 0 | 100 | 0
27180 | TimeSw_Thursday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27181 | TimeSw_Thursday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27182 | TimeSw_Thursday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27183 | TimeSw_Thursday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27184 | TimerSw_Thursday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27185 | TimerSw_Thursday_7_Heat |  | Only for AC | 0 | 100 | 0
27186 | TimeSw_Thursday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27187 | TimeSw_Thursday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27188 | TimeSw_Thursday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27189 | TimeSw_Thursday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27190 | TimerSw_Thursday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27191 | TimerSw_Thursday_8_Heat |  | Only for AC | 0 | 100 | 0
27192 | TimeSw_Friday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27193 | TimeSw_Friday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27194 | TimeSw_Friday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27195 | TimeSw_Friday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27196 | TimerSw_Friday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27197 | TimerSw_Friday_1_Heat |  | Only for AC | 0 | 100 | 0
27198 | TimeSw_Friday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27199 | TimeSw_Friday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27200 | TimeSw_Friday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27201 | TimeSw_Friday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27202 | TimerSw_Friday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27203 | TimerSw_Friday_2_Heat |  | Only for AC | 0 | 100 | 0
27204 | TimeSw_Friday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27205 | TimeSw_Friday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27206 | TimeSw_Friday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27207 | TimeSw_Friday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27208 | TimerSw_Friday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27209 | TimerSw_Friday_3_Heat |  | Only for AC | 0 | 100 | 0
27210 | TimeSw_Friday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27211 | TimeSw_Friday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27212 | TimeSw_Friday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27213 | TimeSw_Friday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27214 | TimerSw_Friday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27215 | TimerSw_Friday_4_Heat |  | Only for AC | 0 | 100 | 0
27216 | TimeSw_Friday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27217 | TimeSw_Friday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27218 | TimeSw_Friday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27219 | TimeSw_Friday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27220 | TimerSw_Friday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27221 | TimerSw_Friday_5_Heat |  | Only for AC | 0 | 100 | 0
27222 | TimeSw_Friday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27223 | TimeSw_Friday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27224 | TimeSw_Friday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27225 | TimeSw_Friday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27226 | TimerSw_Friday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27227 | TimerSw_Friday_6_Heat |  | Only for AC | 0 | 100 | 0
27228 | TimeSw_Friday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27229 | TimeSw_Friday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27230 | TimeSw_Friday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27231 | TimeSw_Friday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27232 | TimerSw_Friday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27233 | TimerSw_Friday_7_Heat |  | Only for AC | 0 | 100 | 0
27234 | TimeSw_Friday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27235 | TimeSw_Friday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27236 | TimeSw_Friday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27237 | TimeSw_Friday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27238 | TimerSw_Friday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27239 | TimerSw_Friday_8_Heat |  | Only for AC | 0 | 100 | 0
27240 | TimeSw_Saturday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27241 | TimeSw_Saturday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27242 | TimeSw_Saturday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27243 | TimeSw_Saturday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27244 | TimerSw_Saturday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27245 | TimerSw_Saturday_1_Heat |  | Only for AC | 0 | 100 | 0
27246 | TimeSw_Saturday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27247 | TimeSw_Saturday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27248 | TimeSw_Saturday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27249 | TimeSw_Saturday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27250 | TimerSw_Saturday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27251 | TimerSw_Saturday_2_Heat |  | Only for AC | 0 | 100 | 0
27252 | TimeSw_Saturday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27253 | TimeSw_Saturday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27254 | TimeSw_Saturday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27255 | TimeSw_Saturday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27256 | TimerSw_Saturday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27257 | TimerSw_Saturday_3_Heat |  | Only for AC | 0 | 100 | 0
27258 | TimeSw_Saturday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27259 | TimeSw_Saturday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27260 | TimeSw_Saturday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27261 | TimeSw_Saturday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27262 | TimerSw_Saturday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27263 | TimerSw_Saturday_4_Heat |  | Only for AC | 0 | 100 | 0
27264 | TimeSw_Saturday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27265 | TimeSw_Saturday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27266 | TimeSw_Saturday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27267 | TimeSw_Saturday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27268 | TimerSw_Saturday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27269 | TimerSw_Saturday_5_Heat |  | Only for AC | 0 | 100 | 0
27270 | TimeSw_Saturday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27271 | TimeSw_Saturday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27272 | TimeSw_Saturday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27273 | TimeSw_Saturday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27274 | TimerSw_Saturday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27275 | TimerSw_Saturday_6_Heat |  | Only for AC | 0 | 100 | 0
27276 | TimeSw_Saturday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27277 | TimeSw_Saturday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27278 | TimeSw_Saturday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27279 | TimeSw_Saturday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27280 | TimerSw_Saturday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27281 | TimerSw_Saturday_7_Heat |  | Only for AC | 0 | 100 | 0
27282 | TimeSw_Saturday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27283 | TimeSw_Saturday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27284 | TimeSw_Saturday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27285 | TimeSw_Saturday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27286 | TimerSw_Saturday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27287 | TimerSw_Saturday_8_Heat |  | Only for AC | 0 | 100 | 0
27288 | TimeSw_Sunday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27289 | TimeSw_Sunday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27290 | TimeSw_Sunday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27291 | TimeSw_Sunday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27292 | TimerSw_Sunday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27293 | TimerSw_Sunday_1_Heat |  | Only for AC | 0 | 100 | 0
27294 | TimeSw_Sunday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27295 | TimeSw_Sunday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27296 | TimeSw_Sunday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27297 | TimeSw_Sunday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27298 | TimerSw_Sunday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27299 | TimerSw_Sunday_2_Heat |  | Only for AC | 0 | 100 | 0
27300 | TimeSw_Sunday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27301 | TimeSw_Sunday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27302 | TimeSw_Sunday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27303 | TimeSw_Sunday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27304 | TimerSw_Sunday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27305 | TimerSw_Sunday_3_Heat |  | Only for AC | 0 | 100 | 0
27306 | TimeSw_Sunday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27307 | TimeSw_Sunday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27308 | TimeSw_Sunday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27309 | TimeSw_Sunday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27310 | TimerSw_Sunday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27311 | TimerSw_Sunday_4_Heat |  | Only for AC | 0 | 100 | 0
27312 | TimeSw_Sunday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27313 | TimeSw_Sunday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27314 | TimeSw_Sunday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27315 | TimeSw_Sunday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27316 | TimerSw_Sunday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27317 | TimerSw_Sunday_5_Heat |  | Only for AC | 0 | 100 | 0
27318 | TimeSw_Sunday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27319 | TimeSw_Sunday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27320 | TimeSw_Sunday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27321 | TimeSw_Sunday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27322 | TimerSw_Sunday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27323 | TimerSw_Sunday_6_Heat |  | Only for AC | 0 | 100 | 0
27324 | TimeSw_Sunday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27325 | TimeSw_Sunday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27326 | TimeSw_Sunday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27327 | TimeSw_Sunday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27328 | TimerSw_Sunday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27329 | TimerSw_Sunday_7_Heat |  | Only for AC | 0 | 100 | 0
27330 | TimeSw_Sunday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27331 | TimeSw_Sunday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27332 | TimeSw_Sunday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27333 | TimeSw_Sunday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27334 | TimerSw_Sunday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27335 | TimerSw_Sunday_8_Heat |  | Only for AC | 0 | 100 | 0

## TIME_SWITCH_YEAR
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Time_switch register (Factory reset set to default)
28000 | TimeSWYear_Enable |  | Time switch 1 Year enable | 0 | 1 | 1 | DISABLE ENABLE
28001 | TimeSwY_1_OnDay |  |  | 1 | 31 | 1
28002 | TimeSwY_1_OnMonth |  |  | 1 | 12 | 1
28003 | TimeSwY_1_OffDay |  |  | 1 | 31 | 1
28004 | TimeSwY_1_OffMonth |  |  | 1 | 31 | 1
28005 | TimeSwY_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28006 | TimeSwY_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28007 | TimeSwY_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28008 | TimeSwY_1_Heat |  | Only for AC | 0 | 100 | 0
28009 | TimeSwY_2_OnDay |  |  | 1 | 31 | 1
28010 | TimeSwY_2_OnMonth |  |  | 1 | 12 | 1
28011 | TimeSwY_2_OffDay |  |  | 1 | 31 | 1
28012 | TimeSwY_2_OffMonth |  |  | 1 | 31 | 1
28013 | TimeSwY_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28014 | TimeSwY_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28015 | TimeSwY_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28016 | TimeSwY_2_Heat |  | Only for AC | 0 | 100 | 0
28017 | TimeSwY_3_OnDay |  |  | 1 | 31 | 1
28018 | TimeSwY_3_OnMonth |  |  | 1 | 12 | 1
28019 | TimeSwY_3_OffDay |  |  | 1 | 31 | 1
28020 | TimeSwY_3_OffMonth |  |  | 1 | 31 | 1
28021 | TimeSwY_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28022 | TimeSwY_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28023 | TimeSwY_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28024 | TimeSwY_3_Heat |  | Only for AC | 0 | 100 | 0
28025 | TimeSwY_4_OnDay |  |  | 1 | 31 | 1
28026 | TimeSwY_4_OnMonth |  |  | 1 | 12 | 1
28027 | TimeSwY_4_OffDay |  |  | 1 | 31 | 1
28028 | TimeSwY_4_OffMonth |  |  | 1 | 31 | 1
28029 | TimeSwY_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28030 | TimeSwY_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28031 | TimeSwY_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28032 | TimeSwY_4_Heat |  | Only for AC | 0 | 100 | 0
28033 | TimeSwY_5_OnDay |  |  | 1 | 31 | 1
28034 | TimeSwY_5_OnMonth |  |  | 1 | 12 | 1
28035 | TimeSwY_5_OffDay |  |  | 1 | 31 | 1
28036 | TimeSwY_5_OffMonth |  |  | 1 | 31 | 1
28037 | TimeSwY_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28038 | TimeSwY_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28039 | TimeSwY_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28040 | TimeSwY_5_Heat |  | Only for AC | 0 | 100 | 0
28041 | TimeSwY_6_OnDay |  |  | 1 | 31 | 1
28042 | TimeSwY_6_OnMonth |  |  | 1 | 12 | 1
28043 | TimeSwY_6_OffDay |  |  | 1 | 31 | 1
28044 | TimeSwY_6_OffMonth |  |  | 1 | 31 | 1
28045 | TimeSwY_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28046 | TimeSwY_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28047 | TimeSwY_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28048 | TimeSwY_6_Heat |  | Only for AC | 0 | 100 | 0
28049 | TimeSwY_7_OnDay |  |  | 1 | 31 | 1
28050 | TimeSwY_7_OnMonth |  |  | 1 | 12 | 1
28051 | TimeSwY_7_OffDay |  |  | 1 | 31 | 1
28052 | TimeSwY_7_OffMonth |  |  | 1 | 31 | 1
28053 | TimeSwY_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28054 | TimeSwY_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28055 | TimeSwY_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28056 | TimeSwY_7_Heat |  | Only for AC | 0 | 100 | 0

## ERROR_LOG_AHU
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Error_log register (Factory reset set to default)
30000 | year
30001 | month
30002 | day
30003 | hour
30004 | min
30005 | sec
30006 | bit0 |  | ON/OFF | 0 | 1 | 0
| bit1 |  | MANUAL | 0 | 1 | 1
| bit2 |  | CAV | 0 | 0 | 0
| bit3 |  | VAV | 0 | 0 | 0
| bit4 |  | DCV | 0 | 1 | 0
| bit5 |  | Fire | 0 | 1 | 0
| bit6 |  | Boost | 0 | 1 | 0
| bit7 |  | Nobody (Nonoccupied) | 0 | 1 | 0
| bit8 |  | Freecooling | 0 | 1 | 0
| bit9 |  | Timeswitch | 0 | 1 | 0
| bit10 |  | Calibration | 0 | 1 | 0
| bit11 |  | Cooldown | 0 | 1 | 0
| bit12 |  | DirectControl | 0 | 1 | 0
| bit13 |  | FilterInfo | 0 | 1 | 0
| bit14 |  | CfgFileError | 0 | 1 | 0
| bit15 |  | Overheat | 0 | 1 | 0
Unit global status2
30007 | bit0 |  | WaterHeater_antifreeze_protection | 0 | 1 | 0
| bit1 |  | WaterHeater waiting for hot water | 0 | 1 | 0
| bit2 |  | WaterHeater waiting for supply air temperature | 0 | 1 | 0
| bit3 |  | WCO searching inlet water temp (cold/hot) | 0 | 1 | 0
| bit4 |  | Recirculation | 0 | 1 | 0
| bit5 |  | Simulation | 0 | 1 | 0
| bit6 |  | Prefreecooling | 0 | 1 | 0
| bit7 |  | Temp Flow Reduction
| bit8 |  | PassiveHouseRestriction
| bit9 |  | AdbActive
Software error1
30008 | bit0 |  | SwFanInletError | 0 | 1
| bit1 |  | SwFanOutletError | 0 | 1
| bit2 |  | SwFilterInletError | 0 | 1
| bit3 |  | SwFilterOutletError | 0 | 1
| bit4 |  | SwFilterInletWarning | 0 | 1
| bit5 |  | SwFilterOutletWarning | 0 | 1
| bit6 |  | SwPreheater1Error | 0 | 1
| bit7 |  | SwPostheater1Error | 0 | 1
| bit8 |  | SwPostheater2Error | 0 | 1
| bit9 |  | SwPreheater2Error | 0 | 1
| bit10 |  | SwAQS SensorError | 0 | 1
| bit11 |  | SwRotaryWheelError | 0 | 1
| bit12 |  | SwADBError | 0 | 1
| bit13 |  | SwDXError | 0 | 1
| bit14 |  | SwDXDefrost | 0 | 1
| bit15 |  | SwCondensateDrain | 0 | 1
Software error2
30009 | bit0 |  | SwGError
| bit1 |  | SwGlobalError
| bit2 |  | SwKError
| bit3 |  | FilterInfo
| bit4 |  | CfgFileError
| bit5 |  | SwFilterHepaError
| bit6 |  | SwFilterHepaWarning
Sensor status1
30010 | bit0 |  | TempEXT1St | 0 | 1 | 0
| bit1 |  | TempEXT2St | 0 | 1 | 0
| bit2 |  | TempEXT3St | 0 | 1 | 0
| bit3 |  | TempEXT4St (module B) | 0 | 0 | 0
| bit4 |  | TempINT0St (module B) | 0 | 0 | 0
| bit5 |  | TempINT1St | 0 | 1 | 0
| bit6 |  | TempINT2St | 0 | 1 | 0
| bit7 |  | TempWInSt (module B) | 0 | 0 | 0
| bit8 |  | TempWOutSt (module B) | 0 | 0 | 0
| bit9 |  | TempRoomSt | 0 | 1 | 0
| bit10 |  | SensorFilterInSt | 0 | 0 | 0
| bit11 |  | SensorFilterOutSt | 0 | 0 | 0
| bit12 |  | SensorFanInletSt | 0 | 0 | 0
| bit13 |  | SensorFanOutSt | 0 | 0 | 0
| bit14 |  | SensorPressSt | 0 | 0 | 0
| bit15 |  | SensorFlowAlaramSt | 0 | 0 | 0
Sensor status2
30011 | bit0 |  | AqsSensorSt | 0 | 0 | 0
| bit1 |  | SensorRHRecSt | 0 | 0 | 0
| bit2 |  | OutsideTempSensorBmsSt | 0 | 0 | 0
| bit3 |  | SensorRHSt | 0 | 0 | 0
| bit4 |  | Sensor Filter Hepa
Input Status1
30012 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 0 | 0
| bit1 |  | Status DI_2_SafetyTherm2 | 0 | 0 | 0
| bit2 |  | Status DI_3_Ext_Control | 0 | 1 | 0
| bit3 |  | Status DI_4_Nobody (FIRE optional) | 0 | 1 | 0
| bit4 |  | Status DI_5_Boost | 0 | 1 | 0
| bit5 |  | Status_DI_TACHO_1 | 0 | 1 | 0
| bit6 |  | Status_DI_TACHO_2 (Rotary wheel error) | 0 | 1 | 0
| bit7 |  | Status_DI_TACHO_3 | 0 | 1 | 0
| bit8 |  | Status_DI_TACHO_4 | 0 | 1 | 0
| bit9 |  | Status_DI_TACHO_5 | 0 | 1 | 0
| bit10 |  | Status_DI_TACHO_6 | 0 | 1 | 0
| bit11 |  | Status_DI_TACHO_7 | 0 | 1 | 0
| bit12 |  | Status_DI_TACHO_8 | 0 | 1 | 0
| bit13 |  | Status_DI_6_ADB_DX_error (module B) | 0 | 1 | 0
| bit14 |  | Status_DI_7_HeatPumpDefrost (module B) | 0 | 1 | 0
| bit15 |  | Status_DI_8_HeatPumpError (module B) | 0 | 1 | 0
Input Status2
30013 | bit0 |  | Status_DI_9_FIRE (module B) | 0 | 1 | 0
| bit1 |  | Status_DI_10_CondensDrain (module B) | 0 | 1 | 0
Output Status1
30014 | bit0 |  | Status_DO_1_Flap_inlet | 0 | 1 | 0
| bit1 |  | Status_DO_2_Flap_outlet | 0 | 1 | 0
| bit2 |  | Status_DO_3_Run_indication | 0 | 1 | 0
| bit3 |  | Status_DO_4_Water_pump (module A) | 0 | 1 | 0
| bit4 |  | Status_DO_5_Heat_cool | 0 | 1 | 0
| bit5 |  | Status_DO_6_Error (module B) | 0 | 1 | 0
| bit6 |  | Status_DO_7_ADB_on_off (module B) | 0 | 1 | 0
| bit7 |  | Status_DO_8_HeatPump_on_off (module B) | 0 | 1 | 0
| bit8 |  | Status_DO_9_WaterPump_on_off (module B) | 0 | 1 | 0
Hardware Status1
30015 | bit0 |  | FRAM
| bit1 |  | EEPROM | 0 | 1 | 0
| bit2 |  | Ethernet | 0 | 1 | 0
| bit3 |  | RTC_Cell | 0 | 1 | 0
| bit4 |  | MainPower | 0 | 1 | 0
| bit5 |  | ControlPanel | 0 | 1 | 0
| bit6 |  | B_module | 0 | 1 | 0
| bit7 |  | C_module_In_Press | 0 | 1 | 0
| bit8 |  | C_module_Out_Press | 0 | 1 | 0
| bit9 |  | C_module_In_Filter_Press | 0 | 1 | 0
| bit10 |  | C_module_Out_Filter_Press | 0 | 1 | 0
| bit11 |  | C_module_Duct_Press | 0 | 1 | 0
| bit12 |  | C_module_C4_Duct_Press | 0 | 1 | 0
| bit13 |  | C_module_RH | 0 | 1 | 0
| bit14 |  | AQS | 0 | 1 | 0
| bit15 |  | USB_over_current | 0 | 1 | 0
Hardware Status2
30016 | bit0 |  | Ethernet_communication | 0 | 1 | 0
| bit9 |  | C_module_Hepa_Press | 0 | 1 | 0
| bit2 |  |  | 0 | 1 | 0
| bit3 |  |  | 0 | 1 | 0
| bit4 |  |  | 0 | 1 | 0
| bit5 |  |  | 0 | 1 | 0
| bit6 |  |  | 0 | 1 | 0
| bit7 |  |  | 0 | 1 | 0
| bit8 |  |  | 0 | 1 | 0
| bit9 |  |  | 0 | 1 | 0
| bit10 |  |  | 0 | 1 | 0
| bit11 |  |  | 0 | 1 | 0
| bit12 |  |  | 0 | 1 | 0
| bit13 |  |  | 0 | 1 | 0
| bit14 |  |  | 0 | 1 | 0
| bit15 |  |  | 0 | 1 | 0
30017 | AirFlowInletFanDemand |  | m3/h (cfm) | 0 | 0xffff | 0
30018 | AirFlowOutletFanDemand |  | m3/h (cfm) | 0 | 0xffff | 0
30019 | AirFlowInletFanManual |  | ‰ of fan power | 0 | 1000 | 0
30020 | AirFlowOutletFanManual |  | ‰ of fan power | 0 | 1000 | 0
30021 | AirFlowInletFan |  | m3/h (cfm) | 0 | 0xffff | 0
30022 | AirFlowOutletFan |  | m3/h (cfm) | 0 | 0xffff | 0
30023 | TempEXT1 |  | °C (°F) | -40 (-40) | 100 (212) | 0
30024 | TempEXT2 |  | °C (°F) | -40 (-40) | 100 (212) | 3
30025 | TempEXT3 |  | °C (°F) | -40 (-40) | 100 (212) | 4
30026 | TempEXT4 |  | °C (°F) (module B) | -40 (-40) | 100 (212) | 5
30027 | TempINT0 |  | °C (°F) (module B) | -40 (-40) | 100 (212) | 20
30028 | TempINT1 |  | °C (°F) | -40 (-40) | 100 (212) | 20
30029 | TempINT2 |  | °C (°F) | -40 (-40) | 100 (212) | 4
30030 | TempWIn |  | °C (°F) (module B) | -40 (-40) | 100 (212) | 22
30031 | TempWOut |  | °C (°F) (module B) | -40 (-40) | 100 (212) | 4
30032 | TempRoom |  | °C (°F) | -40 (-40) | 100 (212) | 21
30033 | SensorFilterIn |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30034 | SensorFilterOut |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30035 | SensorFanInlet |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30036 | SensorFanOut |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30037 | SensorPress |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30038 | SensorFlowAlarm |  |  | 0 | 0 | 0
30039 | AqsSensorValue |  | % | 0 | 100 | 0
30040 | SensorRHRec |  | % | 0 | 100 | 0
30041 | SensorRH |  | % (module C) | 0 | 100 | 0
30042 | PowerPreheater1 |  | % | 0 | 100 | 0
30043 | PowerPreheater2 |  | % (module B) | 0 | 100 | 0
30044 | PowerPostheater1 |  | % | 0 | 100 | 0
30045 | PowerPostheater2 |  | % (module B) | 0 | 100 | 0
30046 | PowerPostheater3 |  | % (module B) | 0 | 100 | 0
30047 | BypassPossition |  | % | 0 | 100 | 0
30048 | Recirculation |  | % (module B) | 0 | 100 | 0
30049 | TempOutsideBMS |  | °C (°F) | -40 (-40) | 100 (212) | 0
30050 | InletFilterPercent |  | % | 0 | 100 | 0
30051 | OutletFilterPercent |  | % | 0 | 100 | 0
30052 | dummy |  |  | 0 | 0xFFFF | 0
30053 | SensorFilterhEPA |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30054 | HepaFilterPercent |  | % | 0 | 100 | 0

## ERROR_LOG_AC
Address | Name | Structure | Info | Min. Value | Max. Value | Enum
Status regiSter - read only (Factory reset no effect)
30000 | day
30001 | month
30002 | hour
30003 | min
Unit global status
30004 | bit0 |  | OFF/ON | 0 | 1
| bit1 |  | Automatic heat | 0 | 1
| bit2 |  | Automatic flow | 0 | 1
| bit3 |  | NightReduction | 0 | 1
| bit4 |  | Timeswitch | 0 | 1
| bit5 |  | Cooldown | 0 | 1
| bit6 |  | WaterHeater_antifreeze_protection | 0 | 1
| bit7 |  | WaterHeater waiting for hot water | 0 | 1
| bit8 |  | SummerHeat | 0 | 1
| bit8 |  | OpenDoor | 0 | 1
| bit10 |  | DoorAfterRunning | 0 | 1
Software error
30005 | bit0 |  | SwFanError | 0 | 1
| bit1 |  | SwFanError1 | 0 | 1
| bit2 |  | SwFilterError | 0 | 1
| bit3 |  | SwFilterWarning | 0 | 1
| bit4 |  | SwHeaterError | 0 | 1
| bit5 |  | SwDXError | 0 | 1
| bit6 |  | SwDXDefrost | 0 | 1
| bit7 |  | SwGlobalError | 0 | 1
| bit8 |  | CfgFileError | 0 | 1
Software error 1
30006 | reserva
Sensor status
30007 | bit0 |  | TempEXT1St | 0 | 1
| bit1 |  | TempEXT3St | 0 | 1
| bit2 |  | TempINT1St | 0 | 1
| bit3 |  | TempWOutSt | 0 | 1
| bit4 |  | TempRoomSt | 0 | 1
| bit5 |  | OutsideTempSensorBmsSt | 0 | 1
| bit6 |  | RoomTempSensorBmsSt | 0 | 1
| bit7 |  | SensorFlowAlaramSt | 0 | 1
Input Status
30008 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 0
| bit1 |  | Status DI_2_SafetyTherm2 | 0 | 0
| bit2 |  | Status DI_3_Ext_Control | 0 | 1
| bit3 |  | Status DI_4_RoomThermostat | 0 | 1
| bit4 |  | Status DI_5_Door | 0 | 1
| bit5 |  | Status_DI_TACHO_1 | 0 | 1
| bit6 |  | Status_DI_TACHO_2 | 0 | 1
| bit7 |  | Status_DI_TACHO_3 | 0 | 1
| bit8 |  | Status_DI_TACHO_4 | 0 | 1
| bit9 |  | Status_DI_TACHO_5 | 0 | 1
| bit10 |  | Status_DI_TACHO_6 | 0 | 1
| bit11 |  | Status_DI_TACHO_7 | 0 | 1
| bit12 |  | Status_DI_TACHO_8 | 0 | 1
| bit13 |  | Status_DI_6_ADB_DX_error | 0 | 1
| bit14 |  | Status_DI_7_HeatPumpDefrost | 0 | 1
| bit15 |  | Status_DI_8_HeatPumpError | 0 | 1
Output Status
30009 | bit0 |  | Status_DO_1_Heat1 | 0 | 1
| bit1 |  | Status_DO_1_Heat2 | 0 | 1
| bit2 |  | Status_DO_3_Run_indication | 0 | 1
| bit3 |  | Status_DO_4_Error | 0 | 1
| bit4 |  | Status_DO_5_Heat_cool | 0 | 1
| bit5 |  | Status_DO_6_Water_pump | 0 | 1
30010 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000
30011 | TempEXT1 |  | °C (°F) | -40 (-40) | 100 (212)
30012 | TempEXT3 |  | °C (°F) | -40 (-40) | 100 (212)
30013 | TempINT1 |  | °C (°F) | -40 (-40) | 100 (212)
30014 | TempWOut |  | °C (°F) | -40 (-40) | 100 (212)
30015 | TempRoom |  | °C (°F) | -40 (-40) | 100 (212)
30016 | SensorFlowAlarm |  |  | 0 | 1
30017 | PowerHeater |  | % | 0 | 100
30018 | TempOutsideBMS |  | °C (°F) | -40 (-40) | 100 (212)
30019 | RoomBMS |  | °C (°F) | -40 (-40) | 101 (212)
30020 | FilterPercent |  | % | 0 | 100
30021 | dummy |  |  | 0 | 0xFFFF
Tacho Board Status
30022 | bit1 |  | Status_DI_TACHO_1 | 0 | 1
| bit2 |  | Status_DI_TACHO_2 | 0 | 1
| bit3 |  | Status_DI_TACHO_3 | 0 | 1
| bit4 |  | Status_DI_TACHO_4 | 0 | 1
| bit5 |  | Status_DI_TACHO_5 | 0 | 1
| bit6 |  | Status_DI_TACHO_6 | 0 | 1
| bit7 |  | Status_DI_TACHO_7 | 0 | 1
| bit8 |  | Status_DI_TACHO_8 | 0 | 1
| bit9 |  | Status_DI_TACHO_9 | 0 | 1
| bit10 |  | Status_DI_TACHO_10 | 0 | 1
30023 | Reserva
30024 | Reserva

## ERROR_LOG_DRIVER
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
29900 | Buffer select |  |  | 0 | 14 | 0
29901 | Bank select |  |  | 0 | 1 | 0
29902 | clear Error log |  |  | 0 | 1 | 0

## NETWORK
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
26000 | IP adress 0.x.x.x |  | IP adress part1 (0x00-0xFF) | 0 | 255 | 192
26001 | IP adress x.0.x.x |  | IP adress part2 (0x00-0xFF) | 0 | 255 | 168
26002 | IP adress x.x.0.x |  | IP adress part3 (0x00-0xFF) | 0 | 255 | 0
26003 | IP adress x.x.x.0 |  | IP adress part4 (0x00-0xFF) | 0 | 255 | 1
26004 | Mask 0.x.x.x |  | Mask part1 (0x00-0xFF) | 0 | 255 | 255
26005 | Mask x.0.x.x |  | Mask part2 (0x00-0xFF) | 0 | 255 | 255
26006 | Mask x.x.0.x |  | Mask part3 (0x00-0xFF) | 0 | 255 | 255
26007 | Mask x.x.x.0 |  | Mask part4 (0x00-0xFF) | 0 | 255 | 0
26008 | Gateway 0.x.x.x |  | Gateway part1 (0x00-0xFF) | 0 | 255 | 192
26009 | Gateway x.0.x.x |  | Gateway part2 (0x00-0xFF) | 0 | 255 | 168
26010 | Gateway x.x.0.x |  | Gateway part3 (0x00-0xFF) | 0 | 255 | 0
26011 | Gateway x.x.x.0 |  | Gateway part4 (0x00-0xFF) | 0 | 255 | 0
26012 | DHCP |  | 0 - DHCP off 1 - DHCP on | 0 | 1 | 0
26013 | ModbusPort |  | Port number 1 - 0xFFFF | 1 | 0xFFFF | 502
26014 | DHCP server |  | 0 - DHCP off 1 - DHCP on | 0 | 1 | 0
26015 | BACnet port |  |  | 1 | 0xFFFF | 0xBAC0
26016 | BACnet device ID MSB |  |  | 0 | 0xFFFF | 0
26017 | BACnet device ID LSB |  |  | 0 | 0xFFFF | 1
26018 | Local Broadcast 0.x.x.x |  | IP adress part1 (0x00-0xFF) | 0 | 255 | 192
26019 | Local Broadcast x.0.x.x |  | IP adress part2 (0x00-0xFF) | 0 | 255 | 168
26020 | Local Broadcast x.x.0.x |  | IP adress part3 (0x00-0xFF) | 0 | 255 | 0
26021 | Local Broadcast x.x.x.0 |  | IP adress part4 (0x00-0xFF) | 0 | 255 | 255

## CFG_UNIT
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
CFG_UNIT (Factory reset no effect)
40000 | CFG_UNIT_PASSWORD
40001 | lenght
40002 | Version
40003 | Serial_number[0]
40004 | Serial_number[1]
40005 | Serial_number[2]
40006 | Serial_number[3]
40007 | Serial_number[4]
40008 | Serial_number[5]
40009 | Serial_number[6]
40010 | Serial_number[7]
40011 | Serial_number[8]
40012 | Serial_number[9]
40013 | Serial_number[10]
40014 | Serial_number[11]
40015 | Serial_number[12]
40016 | Serial_number[13]
40017 | Serial_number[14]
40018 | Serial_number[15]
40019 | Serial_number[16]
40020 | Serial_number[17]
40021 | Serial_number[18]
40022 | Serial_number[19]
40023 | EAN[0]
40024 | EAN[1]
40025 | EAN[2]
40026 | EAN[3]
40027 | EAN[4]
40028 | EAN[5]
40029 | EAN[6]
40030 | EAN[7]
40031 | EAN[8]
40032 | EAN[9]
40033 | EAN[10]
40034 | EAN[11]
40035 | EAN[12]
40036 | EAN[13]
40037 | EAN[14]
40038 | EAN[15]
40039 | EAN[16]
40040 | EAN[17]
40041 | EAN[18]
40042 | EAN[19]
40043 | EAN_sub[0]
40044 | EAN_sub[1]
40045 | EAN_sub[2]
40046 | EAN_sub[3]
40047 | EAN_sub[4]
40048 | EAN_sub[5]
40049 | EAN_sub[6]
40050 | EAN_sub[7]
40051 | EAN_sub[8]
40052 | EAN_sub[9]
40053 | EAN_sub[10]
40054 | EAN_sub[11]
40055 | EAN_sub[12]
40056 | EAN_sub[13]
40057 | EAN_sub[14]
40058 | EAN_sub[15]
40059 | EAN_sub[16]
40060 | EAN_sub[17]
40061 | EAN_sub[18]
40062 | EAN_sub[19]
40063 | EAN_sub[20]
40064 | EAN_sub[21]
40065 | EAN_sub[22]
40066 | EAN_sub[23]
40067 | EAN_sub[24]
40068 | EAN_sub[25]
40069 | EAN_sub[26]
40070 | EAN_sub[27]
40071 | EAN_sub[28]
40072 | EAN_sub[29]
40073 | Factory_id[0]
40074 | Factory_id[1]
40075 | Factory_id[2]
40076 | Id
40077 | Locality
40078 | Default_Language
40079 | Set_GBA
40080 | Name[0]
40081 | Name[1]
40082 | Name[2]
40083 | Name[3]
40084 | Name[4]
40085 | Name[5]
40086 | Name[6]
40087 | Name[7]
40088 | Name[8]
40089 | Name[9]
40090 | Name[10]
40091 | Name_Flow
40092 | Max_Flow
40093 | Min_Flow
40094 | Step_Flow
40095 | Max_constant_press
40096 | Default_Flow
40097 | Default_Temperature
40098 | Recup
40099 | Preheater1
40100 | Preheater2
40101 | Postheater1
40102 | Postheater2
40103 | Bypass
40104 | Recirculation_Unit
40105 | Adiabatic_Unit
40106 | Reserve_Unit_1
40107 | Reserve_Unit_2
40108 | TK1
40109 | TK2
40110 | Fan_Sensor
40111 | Filter_sensor
40112 | Constant_press_sensor
40113 | CP_sensor_site
40114 | RH_dew_point_sensor
40115 | Flow_Alarm_sensor
40116 | K1_fan_inlet
40117 | K1_fan_inlet
40118 | L1_fan_inlet
40119 | K2_fan_inlet
40120 | K2_fan_inlet
40121 | L2_fan_inlet
40122 | K3_fan_inlet
40123 | K3_fan_inlet
40124 | K1_fan_outlet
40125 | K1_fan_outlet
40126 | L1_fan_outlet
40127 | K2_fan_outlet
40128 | K2_fan_outlet
40129 | L2_fan_outlet
40130 | K3_fan_outlet
40131 | K3_fan_outlet
40132 | K1_bypass
40133 | K1_bypass
40134 | K2_bypass
40135 | K2_bypass
40136 | kpfi0
40137 | kpfi0
40138 | kpfi1
40139 | kpfi1
40140 | kpfi2
40141 | kpfi2
40142 | kpfo0
40143 | kpfo0
40144 | kpfo1
40145 | kpfo1
40146 | kpfo2
40147 | kpfo2
40148 | Motor_type
40149 | Motor_PID_P
40150 | Motor_PID_I
40151 | Passive_House
40152 | Off_mode_min_flow
40153 | WhisperAir_limit
40154 | HEPA_filter
40155 | PreferManualOutput
40156 | NumOfDigitalHeaters
40157 | ARC_Timer_service
40158 | NumOfMotors
40159 | FiltersDisableStatus
40160 | Nfc_QR_mode
40161 | motor_max_pwm_limit
40162 | Multi_Cfg
40163 | FunctionDisable_L
40164 | FunctionDisable_H
40165 | Const_MinDuctTemp
40166 | Const_MinSetpointTemp
40167 | UserHID_design
40168 | FunctionVC
40169 | Reserva
40170 | Reserva
40171 | Reserva
40172 | Reserva

## NORDIC_SERVICE
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Nordic service register (Factory reset set to default)
43000 | Valve excercising enable |  |  | 0 | 1 | 0
43001 | Valve excercising time |  |  | 1 | 120 | 60
43002 | Valve bleeding |  |  | 0 | 30 | 0
43003 | Door close fan off enable |  |  | 0 | 1 | 0
43004 | Door close fan off temperature |  |  | 5 | 30 | 20
43005 | Door close fan off delay |  |  | 0 | 120
43006 | reserva |  |  | 0 | 0 | 0
43007 | Door fan limits open min |  |  | 15 | 40 | 20
43008 | Door fan limits open max |  |  | 40 | 100 | 100
43009 | Door fan limits close min |  |  | 15 | 40 | 20
43010 | Door fan limits close max |  |  | 40 | 100 | 100
43011 | Antifreze sensor enable |  |  | 0 | 3 | 3
| bit0 |  | Air | 0 | 1 | 1
| bit1 |  | Water | 0 | 1 | 1
43012 | Water return limit enable |  |  | 0 | 1 | 0
43013 | Water return limit temperature |  |  | 15 | 85 | 50
43014 | Outlet temp limit |  |  | 5 | 30 | 17
43015 | Alarm temp room enable |  |  | 0 | 1 | 0
43016 | Alarm temp room temperature
43017 | Fan off temp room enable |  |  | 0 | 1 | 0
43018 | Fan off temp room |  |  | 1 | 5 | 2
43019 | Damper open |  |  | 0 | 100 | 10
43020 | Damper delay |  |  | 0 | 120 | 30
43021 | Savana fan limits min |  |  | 15 | 40 | 15
43022 | Savana fan limits max |  |  | 40 | 100 | 60
43023 | Outlet limitation room |  |  | 0 | 1
43024 | reserva |  |  | 0 | 0 | 0
43025 | reserva |  |  | 0 | 0 | 0
43026 | reserva |  |  | 0 | 0 | 0

## WIFI_SETTINGS (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Wifi Settings
13000 | State
13001 | Mode
13002 | Mode_1
13003 | NumOfSSID
13004 | NumOfSSID1
13005 | ActiveSSID
13006 | ActiveSSID1
13007 | reserva
13008 | reserva
13009 | reserva
13009 - 13041 | SSID_req
13042 - 13074 | SSID_set
13075 - 13139 | Password_set

## IBUS GateWay Status (hidden)
Address | Name | Structure | Min. Value | Max. Value | Max. Value | Default | Enum
IBUS GateWay Sensors Status
12000 | Gateway_Sensor1_s |  | 0 | 1
| Gateway_Sensor2_s |  | 0 | 1
| Gateway_Sensor3_s |  | 0 | 1
| Gateway_Sensor4_s |  | 0 | 1
| Gateway_Sensor5_s |  | 0 | 1
| Gateway_Sensor6_s |  | 0 | 1
| Gateway_Sensor7_s |  | 0 | 1
| Gateway_Sensor8_s |  | 0 | 1
| Gateway_Sensor9_s |  | 0 | 1
| Gateway_Sensor10_s |  | 0 | 1
| Gateway_Sensor11_s |  | 0 | 1
| Gateway_Sensor12_s |  | 0 | 1
| Gateway_Sensor13_s |  | 0 | 1
| Gateway_Sensor14_s |  | 0 | 1
| Gateway_Sensor15_s |  | 0 | 1
| Gateway_Sensor16_s |  | 0 | 1
12001 | Gateway_Sensor17_s |  | 0 | 1
| Gateway_Sensor18_s |  | 0 | 1
| Gateway_Sensor19_s |  | 0 | 1
| Gateway_Sensor20_s |  | 0 | 1
| Gateway_Sensor21_s |  | 0 | 1
| Gateway_Sensor22_s |  | 0 | 1
| Gateway_Sensor23_s |  | 0 | 1
| Gateway_Sensor24_s |  | 0 | 1
12002 | Sensor1 value |  | 0 | FFFF
12003 | Sensor2 value |  | 0 | FFFF
12004 | Sensor3 value |  | 0 | FFFF
12005 | Sensor4 value |  | 0 | FFFF
12006 | Sensor5 value |  | 0 | FFFF
12007 | Sensor6 value |  | 0 | FFFF
12008 | Sensor7 value |  | 0 | FFFF
12009 | Sensor8 value |  | 0 | FFFF
12010 | Sensor9 value |  | 0 | FFFF
12011 | Sensor10 value |  | 0 | FFFF
12012 | Sensor11 value |  | 0 | FFFF
12013 | Sensor12 value |  | 0 | FFFF
12014 | Sensor13 value |  | 0 | FFFF
12015 | Sensor14 value |  | 0 | FFFF
12016 | Sensor15 value |  | 0 | FFFF
12017 | Sensor16 value |  | 0 | FFFF
12018 | Sensor17 value |  | 0 | FFFF
12019 | Sensor18 value |  | 0 | FFFF
12020 | Sensor19 value |  | 0 | FFFF
12021 | Sensor20 value |  | 0 | FFFF
12022 | Sensor21 value |  | 0 | FFFF
12023 | Sensor22 value |  | 0 | FFFF
12024 | Sensor23 value |  | 0 | FFFF
12025 | Sensor24 value |  | 0 | FFFF

## BMS_TEMP_SENSORS
Address | Name | Info
23000 | RoomBms | write temperature *10
23001 | RoomBms-Status | status of sensor
23002 | OutsideBms | write temperature *10
23003 | OutsideBms-Status | status of sensor

## DIRECT_CONTROL
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
35000 | bit0 |  | Dir_Ctrl_DO_1_Flap_inlet | 0 | 1 | 0 | FLAP_CLOSED FLAP_OPEN
| bit1 |  | Dir_Ctrl_DO_2_Flap_outlet | 0 | 1 | 0 | FLAP_CLOSED FLAP_OPEN
| bit2 |  | Dir_Ctrl_DO_3_Run_indication | 0 | 1 | 0 | RUN_INDICATION NO_RUN
| bit3 |  | Dir_Ctrl_DO_4_Water_pump (module A) | 0 | 1 | 0 | W_PUMP_A_ON W_PUMP_A_OFF
| bit4 |  | Dir_Ctrl_DO_5_Heat_cool | 0 | 1 | 0 | EXCHANGER_COOL EXCHANGER_HEAT
| bit5 |  | Dir_Ctrl_DO_6_Error (module B) | 0 | 1 | 0 | ERROR_B_OK ERROR_B_ERROR
| bit6 |  | Dir_Ctrl_DO_7_ADB_on_off (module B) | 0 | 1 | 0 | ADB_ON ADB_OFF
| bit7 |  | Dir_Ctrl_DO_8_HeatPump_on_off (module B) | 0 | 1 | 0 | HEAT_PUMP_ON HEAT_PUMP_OFF
| bit8 |  | Dir_Ctrl_DO_9_WaterPump_on_off (module B) | 0 | 1 | 0 | W_PUMP_B_ON W_PUMP_B_OFF
35001 | AirFlowInletFanManual |  | Dir_Ctrl_InletFanMan (‰ of fan power) | 0 | 1000 | 0
35002 | AirFlowOutletFanManual |  | Dir_Ctrl_OutletFanMan (‰ of fan power) | 0 | 1000 | 0
35003 | PowerPreheater1 |  | % | 0 | 100 | 0
35004 | PowerPreheater2 |  | % (module B) | 0 | 100 | 0
35005 | PowerPostheater1 |  | % | 0 | 100 | 0
35006 | PowerPostheater2 |  | % (module B) | 0 | 100 | 0
35007 | PowerPostheater3 |  | % (module B) | 0 | 100 | 0
35008 | Recirculation |  | % (module B) | 0 | 100 | 0
35009 | Bypass/Rotary wheel exchanger |  | % | 0 | 100 | 0

## MODE_ERROR_RELAY
Address | Name | Structure | Info | Min. Value | Max. Value | Default
Mode Error Rellay register
44000 | global_en_err_choice |  |  | 0 | 1 | 0
err_relay_en_0
44001 | bit0 |  | ER_FilterInfo | 0 | 1 | 0
| bit1 |  | ER_Reserva2 | 0 | 1 | 0
| bit2 |  | ER_Reserva3 | 0 | 1 | 0
| bit3 |  | ER_SwFanInletError | 0 | 1 | 0
| bit4 |  | ER_SwFanOutletError | 0 | 1 | 0
| bit5 |  | ER_SwFilterInletError | 0 | 1 | 0
| bit6 |  | ER_SwFilterOutletError | 0 | 1 | 0
| bit7 |  | ER_SwPreheater1Error | 0 | 1 | 0
| bit8 |  | ER_SwPostheater1Error | 0 | 1 | 0
| bit9 |  | ER_SwPostheater2Error | 0 | 1 | 0
| bit10 |  | ER_SwPreheater2Error | 0 | 1 | 0
| bit11 |  | ER_SwAQS_SensorError | 0 | 1 | 0
| bit12 |  | ER_SwRotaryWheelError | 0 | 1 | 0
| bit13 |  | ER_SwADBError | 0 | 1 | 0
| bit14 |  | ER_SwDXError | 0 | 1 | 0
| bit15 |  | ER_TempEXT1St | 0 | 1 | 0
err_relay_en_1
44002 | bit0 |  | ER_TempEXT2St | 0 | 1 | 0
| bit1 |  | ER_TempEXT3St | 0 | 1 | 0
| bit2 |  | ER_TempEXT4St_module_B | 0 | 1 | 0
| bit3 |  | ER_TempINT0St_module_B | 0 | 1 | 0
| bit4 |  | ER_TempINT1St | 0 | 1 | 0
| bit5 |  | ER_TempINT2St | 0 | 1 | 0
| bit6 |  | ER_TempWInSt_module_B | 0 | 1 | 0
| bit7 |  | ER_TempWOutSt_module_B | 0 | 1 | 0
| bit8 |  | ER_TempRoomSt | 0 | 1 | 0
| bit9 |  | ER_SensorFilterInSt | 0 | 1 | 0
| bit10 |  | ER_SensorFilterOutSt | 0 | 1 | 0
| bit11 |  | ER_SensorFanInletSt | 0 | 1 | 0
| bit12 |  | ER_SensorFanOutSt | 0 | 1 | 0
| bit13 |  | ER_SensorDuctSt | 0 | 1 | 0
| bit14 |  | ER_SensorC4St | 0 | 1 | 0
| bit15 |  | ER_AqsSensorSt | 0 | 1 | 0
err_relay_en_2
44003 | bit0 |  | ER_SensorRHRecSt | 0 | 1 | 0
| bit1 |  | ER_OutsideTempSensorBmsSt | 0 | 1 | 0
| bit2 |  | ER_SensorRHSt | 0 | 1 | 0
| bit3 |  | ER_SwFilterInletWarning | 0 | 1 | 0
| bit4 |  | ER_SwFilterOutletWarning | 0 | 1 | 0
| bit5 |  | ER_WaterHeater_antifreeze_protection | 0 | 1 | 0
| bit6 |  | ER_WaterHeater_waiting_for_hot_water | 0 | 1 | 0
| bit7 |  | ER_WaterHeater_waiting_for_supply_air_temperature | 0 | 1 | 0
| bit8 |  | ER_WCO_searching_inlet_water_temp_cold_hot | 0 | 1 | 0
| bit9 |  | ER_PreFreeCooling | 0 | 1 | 0
| bit10 |  | ER_TempFlowReduction | 0 | 1 | 0
| bit11 |  | ER_PassiveHouseRestriction | 0 | 1 | 0
| bit12 |  | ER_B_module_error | 0 | 1 | 0
| bit13 |  | ER_SwDXDefrost | 0 | 1 | 0
| bit14 |  | ER_SWwCondensateDrain | 0 | 1 | 0
| bit15 |  | ER_Status_G_modul | 0 | 1 | 0
err_relay_en_3
44004 | bit0 |  | ER_Global_Error | 0 | 1 | 0
| bit1 |  | ER_Status_K_modul | 0 | 1 | 0
| bit2 |  | ER_SensorFlowSt | 0 | 1 | 0
| bit3 |  | ER_SensorFilterHepaInSt | 0 | 1 | 0
| bit4 |  | ER_SwFilterHepaError | 0 | 1 | 0
| bit5 |  | ER_SwFilterHepaWarning | 0 | 1 | 0
| bit6 |  | ER_FW_update_available | 0 | 1 | 0
| bit7 |  | ER_SwFanError | 0 | 1 | 0
| bit8 |  | ER_SwFilterError | 0 | 1 | 0
| bit9 |  | ER_SwHeaterError | 0 | 1 | 0
| bit10 |  | ER_Outside_St | 0 | 1 | 0
| bit11 |  | ER_Outlet_St | 0 | 1 | 0
| bit12 |  | ER_Inlet_St | 0 | 1 | 0
| bit13 |  | ER_TempWOutSt | 0 | 1 | 0
| bit14 |  | ER_TempRoom_2_St | 0 | 1 | 0
| bit15 |  | ER_OutsideTempSensorBms_2_St | 0 | 1 | 0
err_relay_en_4
44005 | bit0 |  | ER_RoomTempSensorBmsSt | 0 | 1 | 0
| bit1 |  | ER_SensorFlowAlaramSt | 0 | 1 | 0
| bit2 |  | ER_SwFilterWarning | 0 | 1 | 0
| bit3 |  | ER_HeaterUnderPower | 0 | 1 | 0
| bit4 |  | ER_Communication_failure | 0 | 1 | 0
| bit5 |  | ER_Modbus_Gateway_communication_failure | 0 | 1 | 0
| bit6 |  | ER_Alarm_temp_room | 0 | 1 | 0
| bit7 |  | ER_SensorRH_EXT1St | 0 | 1 | 0
| bit8 |  | ER_SensorRH_EXT2St | 0 | 1 | 0
| bit9 |  | ER_SensorRH_INT1St | 0 | 1 | 0
| bit10 |  | ER_SensorRH_INT2St | 0 | 1 | 0
| bit11 |  | ER_Reserve_11 | 0 | 1 | 0
| bit12 |  | ER_Reserve_12 | 0 | 1 | 0
| bit13 |  | ER_Reserve_13 | 0 | 1 | 0
| bit14 |  | ER_Reserve_14 | 0 | 1 | 0
| bit15 |  | ER_Reserve_15 | 0 | 1 | 0

## SIMULATION (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
36000

## FILTER_CALIBRATION (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
37000

## EEFICIENCY AND SAVINGS (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
| AvarageRecEfficiency |  | % | 0 | 100
| AvarageAirflow |  | % | 0 | 100